## eWind Modbus Documentation
eWind modbus list
Coil | Symbol | Description | Name | Type | R/W | Enumeration | Multiplier | Min,Max | Notes
Coil 0 | COIL_STOP | Stop | Stop the machine | uint16 | R/W | onoff | 1
Coil 1 | COIL_AWAY | Away mode | mode | uint16 | R/W | onoff | 1
Coil 3 | COIL_OVP | Overpressure mode | Enable overpressure mode | uint16 | R/W | enabledisable | 1
Coil 6 | COIL_MAX_H | Max heating | Force the machine to heat at maximum effect. | uint16 | R/W | onoff | 1
Coil 7 | COIL_MAX_C | Max cooling | Force the machine to cool at maximum effect. | uint16 | R/W | onoff | 1
Coil 8 | COIL_CO2_BOOST_EN | CO₂ boosting | Enable or disable CO₂ boosting | uint16 | R/W | enabledisable | 1 |  | When setting this coil to 1, HREG_AI1_TYPE is changed to CO2. When set to to 0, AI1 type is changed to RH
Coil 9 | COIL_RH_BOOST_EN | %RH boosting | Enable or disable humidity boosting | uint16 | R/W | enabledisable | 1
Coil 10 | COIL_M_BOOST | Manual boost | Boost the fanspeeds to 100\% for a period of time | uint16 | R/W | onoff | 1
Coil 11 | COIL_TEMP_BOOST_EN | Temperature boost | Enable or disable temperature boosting | uint16 | R/W | enabledisable | 1
Coil 18 | COIL_AWAY_H | Heating | Supply air heating enabled or disabled in Away mode | uint16 | R/W | enabledisable | 1
Coil 19 | COIL_AWAY_C | Cooling | Supply air cooling enabled or disabled in Away mode | uint16 | R/W | enabledisable | 1
Coil 30 | COIL_LTO_ON |  | Heat recycler state (running=1, stopped = 0) | uint16 | R/W | none | 1
Coil 32 | COIL_HEAT_ON |  | Element status of after-heater (On = 1, Off = 0) | uint16 | R/W | none | 1
Coil 36 | COIL_TEMP_DECREASE | Decrease temperature | Temperature decrease function desc | uint16 | R/W | onoff | 1 |  | Temperature offset from setpoint is defined in reg 172
Coil 40 | COIL_ECO_MODE | Eco mode | Eco mode desc. | uint16 | R/W | onoff | 1
Coil 41 | COIL_ALARM_A | Alarm A | Alarm of class A active desc. | uint16 | R | onoff | 1
Coil 42 | COIL_ALARM_B | Alarm B | Alarm of class B active desc. | uint16 | R | onoff | 1
Coil 49 | COIL_SERVICE_EN | Service reminder | Service reminder enabled | uint16 | R/W | enabledisable | 1
Register | Symbol | Description | Name | Type | R/W | Enumeration | Multiplier | Min,Max | Notes
Holding reg 6 | HREG_T_FRS | Fresh air | Outside air temperature at the unit (sensor TE01) | int16 | R | none | 10
Holding reg 7 | HREG_T_SPLY_LTO | Supply air after HRC | Supply air temperature after heat recovery (sensor TE05) | int16 | R | none | 10
Holding reg 8 | HREG_T_SPLY | Supply air | Supply air temperature after supply air heater (sensor TE10) | int16 | R | none | 10
Holding reg 9 | HREG_T_WST | Exhaust air | Exhaust air temperature (sensor TE32) | int16 | R | none | 10
Holding reg 10 | HREG_T_EXT | Extract air temperature | Extract air temperature from building at the unit (sensor TE30) | int16 | R | none | 10
Holding reg 12 | HREG_T_WR | Return water | Return water temperature in supply air heater (sensor TE45) | int16 | R | none | 10
Holding reg 13 | HREG_HUM_EXT | Air humidity | Extract air relative humidity \%RH at the unit (sensor RH30) | uint16 | R | none | 1
Holding reg 23 | HREG_AI1_RES | Calculated value | Calculated result | uint16 | R | none | 1 |  | Conversion depends on HREG_AIx_RL, HREG_AIx_RH, HREG_AIx_VL, HREG_AIx_VH
Holding reg 29 | HREG_LTO_N_SPLY | Heat recovery efficiency, supply air | Supply air temperature efficiency. Calculated from outside air-, supply air after heat recovery- and extract air temperature | uint16 | R | none | 1
Holding reg 30 | HREG_LTO_N_EXT | Heat recovery efficiency, exhaust air | Extract air temperature efficiency. Calculated from extract air-, exhaust air- and outside air temperature. In HP-units calculated from HRC extract air-, exhaust air- and outside air temperature | uint16 | R | none | 1
Holding reg 35 | HREG_RH_MEAN | Average air humidity, 48h | Extract air 48h mean relative humidity \%RH at the unit (sensor RH30). Updated every hour | uint16 | R | none | 1
Holding reg 44 | HREG_MODE | Status | All current states of unit, eg. Home, Central vacuum cleaner, HP/EDX defrost etc. | bitfield | R | mode | 1
Holding reg 45 | HREG_EXTMODE | Temperature controller | Displays current state of temperature controller; cooling, heat recovery, heating or none. | enumeration | R | tempstep | 1
Holding reg 48 | HREG_DISPLAY_SP |  | Temperature controller setpoint shown to user | int16 | R | none | 10
Holding reg 49 | HREG_OUTPUT | Temperature controller output | -100...-1=cooling, 0=nothing, 1...100=heat recovery, 101...200=additional heating or heat pump, 201...300=additional heating in heat pump units | int16 | R | none | 1
Holding reg 50 | HREG_DISPLAY_FANSPEED | Fan speed control | Fan speed level 1-4 set via panel | uint16 | R | escfanspeed | 1
Holding reg 51 | HREG_FAN_TF_BASIC | Supply air | TF fan speed corresponding to fan speed level 2 | uint16 | R/W | none | 1 | 20,100
Holding reg 52 | HREG_FAN_PF_BASIC | Extract air | PF fan speed corresponding to fan speed level 2 | uint16 | R/W | none | 1 | 20,100
Holding reg 54 | HREG_OVP_TF | Supply air | Supply air fan speed in manual overpressure mode | uint16 | R/W | none | 1 | 20,100
Holding reg 55 | HREG_OVP_PF | Extract air | Extract air fan speed in manual overpressure mode | uint16 | R/W | none | 1 | 20,100
Holding reg 56 | HREG_OVP_TIME | Overpressure duration | Duration of manual overpressure function in minutes | uint16 | R/W | none | 1 | 1,60 | The value in this register is overwritten by the default value in HREG_OVP_TIME_DEF at system startup.
Holding reg 57 | HREG_OVP_TIME_DEF | Overpressure time | Duration of overpressure function, in minutes, default value | uint16 | R/W | none | 1 | 1,60
Holding reg 66 | HREG_M_BOOST_TIME | Boost time | Duration of manual boosting function in minutes | uint16 | R/W | none | 1 | 1,500
Holding reg 67 | HREG_M_BOOST_TF_FANSPEED | Supply air | Supply air fan speed in manual boosting mode | uint16 | R/W | none | 1 | 20,100
Holding reg 68 | HREG_M_BOOST_PF_FANSPEED | Extract air | Extract air fan speed in manual boosting mode | uint16 | R/W | none | 1 | 20,100
Holding reg 69 | HREG_RH_LIM | %RH boosting threshold value | Boosting starts when relative humidity exceeds this limit during winter mode | uint16 | R/W | none | 1 | 10,100
Holding reg 70 | HREG_RH_LIM_A | Threshold 48h %RH | Boosting starts when relative humidity exceeds 48h average humidity with this threshold during summer mode | uint16 | R/W | none | 1 | 0,100
Holding reg 72 | HREG_RH_MAX_TF_FANSPEED | TF fanspeed fanspeed for fan level 3 | Maximum TF fanspeed for fanspeed level 3, RH and CO2 boosting | uint16 | R/W | none | 1 | 20,100
Holding reg 74 | HREG_RH_MAX_PF_FANSPEED | PF fanspeed for fan speed level 3 | Maximum PF fanspeed for fanspeed level 3, RH and CO2 boosting | uint16 | R/W | none | 1 | 20,100
Holding reg 76 | HREG_CO2_LIM | CO₂ boosting threshold | Boosting starts when carbon dioxide levels exceed this limit | uint16 | R/W | none | 1 | 400,3000
Holding reg 100 | HREG_AWAY_TF_FANSPEED | TF fan speed in fan level 1 | Supply air fan speed in Away mode | uint16 | R/W | none | 1 | 20,100
Holding reg 101 | HREG_AWAY_TEMP_D | Temperature drop | Temperature drop in Away mode | int16 | R/W | none | 10 | 0,150
Holding reg 102 | HREG_AWAY_PF_FANSPEED | PF fan speed in fan level 1 | Extract air fan speed in Away mode | uint16 | R/W | none | 1 | 20,100
Holding reg 103 | HREG_AWAYL_TEMP_D | Temperature drop | mode | int16 | R/W | none | 10 | 0,150
Holding reg 104 | HREG_AI1_TYPE | Sensor type | Type of external sensor in AI1. | uint16 | R/W | analogIn | 1
Holding reg 110 | HREG_AI1_VL | Voltage low | AI1 voltage low when AI1 type is RH transmitter | uint16 | R/W | none | 10 | 0,100
Holding reg 114 | HREG_AI5_VL | Voltage low | AI1 voltage low when AI1 type is CO2 transmitter | uint16 | R/W | none | 10 | 0,100
Holding reg 116 | HREG_AI1_VH | Voltage high | AI1 voltage high when AI1 type is RH transmitter | uint16 | R/W | none | 10 | 0,100
Register | Symbol | Description | Name | Type | R/W | Enumeration | Multiplier | Min,Max | Notes
Holding reg 120 | HREG_AI5_VH | Voltage high | AI1 voltage high when AI1 type CO2 transmitter | uint16 | R/W | none | 10 | 0,100
Holding reg 122 | HREG_AI1_RL | Voltage low, effect | AI1 output value at 0V when AI1 type is RH transmitter | int16 | R/W | none | 1
Holding reg 126 | HREG_AI5_RL | Voltage low, effect | AI1 output value at 0V when type is CO2_1 | int16 | R/W | none | 1
Holding reg 128 | HREG_AI1_RH | Voltage high, effect | AI1 output value at 10V when AI1 type is RH transmitter | int16 | R/W | none | 1
Holding reg 132 | HREG_AI5_RH | Voltage high, effect | AI1 output value at 10V when type is CO2_1 | int16 | R/W | none | 1
Holding reg 134 | HREG_TE01_24H_AVG | Average outside temperature | 24-hour outside temperature average | int16 | R | none | 10
Holding reg 135 | HREG_T_SETPOINT | Supply air setpoint | Desired setpoint set by the user | int16 | R/W | none | 10 | 0,500
Holding reg 137 | HREG_TE01_SUMMER_WINTER_THRESHOLD | Summer/winter threshold temperature | Outside air 24h average temperature; in summer mode extract air 48h average humidity, in winter mode a fixed \%RH threshold | int16 | R/W | none | 10 | -100,150
Holding reg 138 | HREG_TC1_SP_MIN | Minimum temperature of supply air | Temperature controller tries to keep supply air temperature above this value in constant extract- and room temperature control modes | int16 | R/W | none | 10 | 100,500
Holding reg 139 | HREG_TC1_SP_MAX | Maximum temperature of supply air | Temperature controller tries to keep supply air temperature below this value in constant extract- and room temperature control modes | int16 | R/W | none | 10 | 100,500
Holding reg 164 | HREG_COOL_BLOCK_T | Outside temperature limit for cooling | Active- or free cooling with heat recovery wheel is not allowed below this temperature | int16 | R/W | none | 10 | 50,400
Holding reg 172 | HREG_TEMP_DECREASE_VAL | Temperature decrease | Number of degrees, under which the temperature should be maintained when temperature decrease function is on | int16 | R/W | none | 10 | 0,150 | Low limit can be negative to enable temperature increase function.
Holding reg 196 | HREG_HEAT_BLOCK_T | Outside temperature limit for heating | Active heating of supply air is not allowed when this temperature is exceeded | int16 | R/W | none | 10 | -50,250
Holding reg 343 | HREG_UPTIME | System uptime | Number of minutes since system was started. Note: count will reset to zero after approximately 45 days | uint16 | R/W | none | 1 |  | Warning: the count is approximative, it should not be used for time-keeping purposes
Holding reg 348 | HREG_PANEL_BUS_NUM_SLAVES | Number of active panel bus units | The number of modbus slaves detected, updated every minute | uint16 | R/W | none | 1
Holding reg 354 | HREG_BOOTLOADER_VERSION | Bootloader version | Bootloader version (desc.) | uint16 | R/W | none | 1 |  | Reserved for future use on ESC.
Holding reg 385 | HREG_ALARM1_ALMTYPE |  | Alarm 1 (newest) alarm type | uint16 | R/W | alarmtypes | 1
Holding reg 386 | HREG_ALARM1_STATECLASS |  | This defines the status (low byte) and class of the alarm (high byte) | uint16 | R/W | alarmstate | 1
Holding reg 387 | HREG_ALARM1_YY |  | Alarm year | uint16 | R/W | none | 1
Holding reg 388 | HREG_ALARM1_MM |  | Alarm month | uint16 | R/W | none | 1
Holding reg 389 | HREG_ALARM1_DD |  | Alarm day | uint16 | R/W | none | 1
Holding reg 390 | HREG_ALARM1_HH |  | Alarm hour | uint16 | R/W | none | 1
Holding reg 391 | HREG_ALARM1_MI |  |  | uint16 | R/W | none | 1
Holding reg 392 | HREG_ALARM2_ALMTYPE |  | / | uint16 | R/W | alarmtypes | 1
Holding reg 393 | HREG_ALARM2_STATECLASS |  | Holding register 393/ | uint16 | R/W | alarmstate | 1
Holding reg 394 | HREG_ALARM2_YY |  | Holding register 394/ | uint16 | R/W | none | 1
Holding reg 395 | HREG_ALARM2_MM |  | Holding register 395/ | uint16 | R/W | none | 1
Holding reg 396 | HREG_ALARM2_DD |  | Holding register 396/ | uint16 | R/W | none | 1
Holding reg 397 | HREG_ALARM2_HH |  | Holding register 397/ | uint16 | R/W | none | 1
Holding reg 398 | HREG_ALARM2_MI |  | Holding register 398/ | uint16 | R/W | none | 1
Holding reg 399 | HREG_ALARM3_ALMTYPE |  | Holding register 399/ | uint16 | R/W | alarmtypes | 1
Holding reg 400 | HREG_ALARM3_STATECLASS |  | Holding register 400/ | uint16 | R/W | alarmstate | 1
Holding reg 401 | HREG_ALARM3_YY |  | Holding register 401/ | uint16 | R/W | none | 1
Holding reg 402 | HREG_ALARM3_MM |  | Holding register 402/ | uint16 | R/W | none | 1
Holding reg 403 | HREG_ALARM3_DD |  | Holding register 403/ | uint16 | R/W | none | 1
Holding reg 404 | HREG_ALARM3_HH |  | Holding register 404/ | uint16 | R/W | none | 1
Holding reg 405 | HREG_ALARM3_MI |  | Holding register 405/ | uint16 | R/W | none | 1
Holding reg 406 | HREG_ALARM4_ALMTYPE |  | Holding register 406/ | uint16 | R/W | alarmtypes | 1
Holding reg 407 | HREG_ALARM4_STATECLASS |  | Holding register 407/ | uint16 | R/W | alarmstate | 1
Holding reg 408 | HREG_ALARM4_YY |  | Holding register 408/ | uint16 | R/W | none | 1
Holding reg 409 | HREG_ALARM4_MM |  | Holding register 409/ | uint16 | R/W | none | 1
Holding reg 410 | HREG_ALARM4_DD |  | Holding register 410/ | uint16 | R/W | none | 1
Holding reg 411 | HREG_ALARM4_HH |  | Holding register 411/ | uint16 | R/W | none | 1
Holding reg 412 | HREG_ALARM4_MI |  | Holding register 412/ | uint16 | R/W | none | 1
Holding reg 413 | HREG_ALARM5_ALMTYPE |  | Holding register 413/ | uint16 | R/W | alarmtypes | 1
Holding reg 414 | HREG_ALARM5_STATECLASS |  | Holding register 414/ | uint16 | R/W | alarmstate | 1
Holding reg 415 | HREG_ALARM5_YY |  | Holding register 415/ | uint16 | R/W | none | 1
Holding reg 416 | HREG_ALARM5_MM |  | Holding register 416/ | uint16 | R/W | none | 1
Holding reg 417 | HREG_ALARM5_DD |  | Holding register 417/ | uint16 | R/W | none | 1
Holding reg 418 | HREG_ALARM5_HH |  | Holding register 418/ | uint16 | R/W | none | 1
Holding reg 419 | HREG_ALARM5_MI |  | Holding register 419/ | uint16 | R/W | none | 1
Holding reg 420 | HREG_ALARM6_ALMTYPE |  | Holding register 420/ | uint16 | R/W | alarmtypes | 1
Holding reg 421 | HREG_ALARM6_STATECLASS |  | Holding register 421/ | uint16 | R/W | alarmstate | 1
Holding reg 422 | HREG_ALARM6_YY |  | Holding register 422/ | uint16 | R/W | none | 1
Holding reg 423 | HREG_ALARM6_MM |  | Holding register 423/ | uint16 | R/W | none | 1
Holding reg 424 | HREG_ALARM6_DD |  | Holding register 424/ | uint16 | R/W | none | 1
Holding reg 425 | HREG_ALARM6_HH |  | Holding register 425/ | uint16 | R/W | none | 1
Holding reg 426 | HREG_ALARM6_MI |  | Holding register 426/ | uint16 | R/W | none | 1
Holding reg 427 | HREG_ALARM7_ALMTYPE |  | Holding register 427/ | uint16 | R/W | alarmtypes | 1
Holding reg 428 | HREG_ALARM7_STATECLASS |  | Holding register 428/ | uint16 | R/W | alarmstate | 1
Holding reg 429 | HREG_ALARM7_YY |  | Holding register 429/ | uint16 | R/W | none | 1
Holding reg 430 | HREG_ALARM7_MM |  | Holding register 430/ | uint16 | R/W | none | 1
Holding reg 431 | HREG_ALARM7_DD |  | Holding register 431/ | uint16 | R/W | none | 1
Holding reg 432 | HREG_ALARM7_HH |  | Holding register 432/ | uint16 | R/W | none | 1
Register | Symbol | Description | Name | Type | R/W | Enumeration | Multiplier | Min,Max | Notes
Holding reg 433 | HREG_ALARM7_MI |  | Holding register 433/ | uint16 | R/W | none | 1
Holding reg 434 | HREG_ALARM8_ALMTYPE |  | Holding register 434/ | uint16 | R/W | alarmtypes | 1
Holding reg 435 | HREG_ALARM8_STATECLASS |  | Holding register 435/ | uint16 | R/W | alarmstate | 1
Holding reg 436 | HREG_ALARM8_YY |  | Holding register 436/ | uint16 | R/W | none | 1
Holding reg 437 | HREG_ALARM8_MM |  | Holding register 437/ | uint16 | R/W | none | 1
Holding reg 438 | HREG_ALARM8_DD |  | Holding register 438/ | uint16 | R/W | none | 1
Holding reg 439 | HREG_ALARM8_HH |  | Holding register 439/ | uint16 | R/W | none | 1
Holding reg 440 | HREG_ALARM8_MI |  | Holding register 440/ | uint16 | R/W | none | 1
Holding reg 441 | HREG_ALARM9_ALMTYPE |  | Holding register 441/ | uint16 | R/W | alarmtypes | 1
Holding reg 442 | HREG_ALARM9_STATECLASS |  | Holding register 442/ | uint16 | R/W | alarmstate | 1
Holding reg 443 | HREG_ALARM9_YY |  | Holding register 443/ | uint16 | R/W | none | 1
Holding reg 444 | HREG_ALARM9_MM |  | Holding register 444/ | uint16 | R/W | none | 1
Holding reg 445 | HREG_ALARM9_DD |  | Holding register 445/ | uint16 | R/W | none | 1
Holding reg 446 | HREG_ALARM9_HH |  | Holding register 446/ | uint16 | R/W | none | 1
Holding reg 447 | HREG_ALARM9_MI |  | Holding register 447/ | uint16 | R/W | none | 1
Holding reg 448 | HREG_ALARM10_ALMTYPE |  | Holding register 448/ | uint16 | R/W | alarmtypes | 1
Holding reg 449 | HREG_ALARM10_STATECLASS |  | Holding register 449/ | uint16 | R/W | alarmstate | 1
Holding reg 450 | HREG_ALARM10_YY |  | Holding register 450/ | uint16 | R/W | none | 1
Holding reg 451 | HREG_ALARM10_MM |  | Holding register 451/ | uint16 | R/W | none | 1
Holding reg 452 | HREG_ALARM10_DD |  | Holding register 452/ | uint16 | R/W | none | 1
Holding reg 453 | HREG_ALARM10_HH |  | Holding register 453/ | uint16 | R/W | none | 1
Holding reg 454 | HREG_ALARM10_MI |  | Holding register 454/ | uint16 | R/W | none | 1
Holding reg 455 | HREG_ALARM11_ALMTYPE |  | Holding register 455/ | uint16 | R/W | alarmtypes | 1
Holding reg 456 | HREG_ALARM11_STATECLASS |  | Holding register 456/ | uint16 | R/W | alarmstate | 1
Holding reg 457 | HREG_ALARM11_YY |  | Holding register 457/ | uint16 | R/W | none | 1
Holding reg 458 | HREG_ALARM11_MM |  | Holding register 458/ | uint16 | R/W | none | 1
Holding reg 459 | HREG_ALARM11_DD |  | Holding register 459/ | uint16 | R/W | none | 1
Holding reg 460 | HREG_ALARM11_HH |  | Holding register 460/ | uint16 | R/W | none | 1
Holding reg 461 | HREG_ALARM11_MI |  | Holding register 461/ | uint16 | R/W | none | 1
Holding reg 462 | HREG_ALARM12_ALMTYPE |  | Holding register 462/ | uint16 | R/W | alarmtypes | 1
Holding reg 463 | HREG_ALARM12_STATECLASS |  | Holding register 463/ | uint16 | R/W | alarmstate | 1
Holding reg 464 | HREG_ALARM12_YY |  | Holding register 464/ | uint16 | R/W | none | 1
Holding reg 465 | HREG_ALARM12_MM |  | Holding register 465/ | uint16 | R/W | none | 1
Holding reg 466 | HREG_ALARM12_DD |  | Holding register 466/ | uint16 | R/W | none | 1
Holding reg 467 | HREG_ALARM12_HH |  | Holding register 467/ | uint16 | R/W | none | 1
Holding reg 468 | HREG_ALARM12_MI |  | Holding register 468/ | uint16 | R/W | none | 1
Holding reg 469 | HREG_ALARM13_ALMTYPE |  | Holding register 469/ | uint16 | R/W | alarmtypes | 1
Holding reg 470 | HREG_ALARM13_STATECLASS |  | Holding register 470/ | uint16 | R/W | alarmstate | 1
Holding reg 471 | HREG_ALARM13_YY |  | Holding register 471/ | uint16 | R/W | none | 1
Holding reg 472 | HREG_ALARM13_MM |  | Holding register 472/ | uint16 | R/W | none | 1
Holding reg 473 | HREG_ALARM13_DD |  | Holding register 473/ | uint16 | R/W | none | 1
Holding reg 474 | HREG_ALARM13_HH |  | Holding register 474/ | uint16 | R/W | none | 1
Holding reg 475 | HREG_ALARM13_MI |  | Holding register 475/ | uint16 | R/W | none | 1
Holding reg 476 | HREG_ALARM14_ALMTYPE |  | Holding register 476/ | uint16 | R/W | alarmtypes | 1
Holding reg 477 | HREG_ALARM14_STATECLASS |  | Holding register 477/ | uint16 | R/W | alarmstate | 1
Holding reg 478 | HREG_ALARM14_YY |  | Holding register 478/ | uint16 | R/W | none | 1
Holding reg 479 | HREG_ALARM14_MM |  | Holding register 479/ | uint16 | R/W | none | 1
Holding reg 480 | HREG_ALARM14_DD |  | Holding register 480/ | uint16 | R/W | none | 1
Holding reg 481 | HREG_ALARM14_HH |  | Holding register 481/ | uint16 | R/W | none | 1
Holding reg 482 | HREG_ALARM14_MI |  | Holding register 482/ | uint16 | R/W | none | 1
Holding reg 483 | HREG_ALARM15_ALMTYPE |  | Holding register 483/ | uint16 | R/W | alarmtypes | 1
Holding reg 484 | HREG_ALARM15_STATECLASS |  | Holding register 484/ | uint16 | R/W | alarmstate | 1
Holding reg 485 | HREG_ALARM15_YY |  | Holding register 485/ | uint16 | R/W | none | 1
Holding reg 486 | HREG_ALARM15_MM |  | Holding register 486/ | uint16 | R/W | none | 1
Holding reg 487 | HREG_ALARM15_DD |  | Holding register 487/ | uint16 | R/W | none | 1
Holding reg 488 | HREG_ALARM15_HH |  | Holding register 488/ | uint16 | R/W | none | 1
Holding reg 489 | HREG_ALARM15_MI |  | Holding register 489/ | uint16 | R/W | none | 1
Holding reg 490 | HREG_ALARM16_ALMTYPE |  | Holding register 490/ | uint16 | R/W | alarmtypes | 1
Holding reg 491 | HREG_ALARM16_STATECLASS |  | Holding register 491/ | uint16 | R/W | alarmstate | 1
Holding reg 492 | HREG_ALARM16_YY |  | Holding register 492/ | uint16 | R/W | none | 1
Holding reg 493 | HREG_ALARM16_MM |  | Holding register 493/ | uint16 | R/W | none | 1
Holding reg 494 | HREG_ALARM16_DD |  | Holding register 494/ | uint16 | R/W | none | 1
Holding reg 495 | HREG_ALARM16_HH |  | Holding register 495/ | uint16 | R/W | none | 1
Holding reg 496 | HREG_ALARM16_MI |  | Holding register 496/ | uint16 | R/W | none | 1
Register | Symbol | Description | Name | Type | R/W | Enumeration | Multiplier | Min,Max | Notes
Holding reg 497 | HREG_ALARM17_ALMTYPE |  | Holding register 497/ | uint16 | R/W | alarmtypes | 1
Holding reg 498 | HREG_ALARM17_STATECLASS |  | Holding register 498/ | uint16 | R/W | alarmstate | 1
Holding reg 499 | HREG_ALARM17_YY |  | Holding register 499/ | uint16 | R/W | none | 1
Holding reg 500 | HREG_ALARM17_MM |  | Holding register 500/ | uint16 | R/W | none | 1
Holding reg 501 | HREG_ALARM17_DD |  | Holding register 501/ | uint16 | R/W | none | 1
Holding reg 502 | HREG_ALARM17_HH |  | Holding register 502/ | uint16 | R/W | none | 1
Holding reg 503 | HREG_ALARM17_MI |  | Holding register 503/ | uint16 | R/W | none | 1
Holding reg 504 | HREG_ALARM18_ALMTYPE |  | Holding register 504/ | uint16 | R/W | alarmtypes | 1
Holding reg 505 | HREG_ALARM18_STATECLASS |  | Holding register 505/ | uint16 | R/W | alarmstate | 1
Holding reg 506 | HREG_ALARM18_YY |  | Holding register 506/ | uint16 | R/W | none | 1
Holding reg 507 | HREG_ALARM18_MM |  | Holding register 507/ | uint16 | R/W | none | 1
Holding reg 508 | HREG_ALARM18_DD |  | Holding register 508/ | uint16 | R/W | none | 1
Holding reg 509 | HREG_ALARM18_HH |  | Holding register 509/ | uint16 | R/W | none | 1
Holding reg 510 | HREG_ALARM18_MI |  | Holding register 510/ | uint16 | R/W | none | 1
Holding reg 511 | HREG_ALARM19_ALMTYPE |  | Holding register 511/ | uint16 | R/W | alarmtypes | 1
Holding reg 512 | HREG_ALARM19_STATECLASS |  | Holding register 512/ | uint16 | R/W | alarmstate | 1
Holding reg 513 | HREG_ALARM19_YY |  | Holding register 513/ | uint16 | R/W | none | 1
Holding reg 514 | HREG_ALARM19_MM |  | Holding register 514/ | uint16 | R/W | none | 1
Holding reg 515 | HREG_ALARM19_DD |  | Holding register 515/ | uint16 | R/W | none | 1
Holding reg 516 | HREG_ALARM19_HH |  | Holding register 516/ | uint16 | R/W | none | 1
Holding reg 517 | HREG_ALARM19_MI |  | Holding register 517/ | uint16 | R/W | none | 1
Holding reg 518 | HREG_ALARM20_ALMTYPE |  | Holding register 518/ | uint16 | R/W | alarmtypes | 1
Holding reg 519 | HREG_ALARM20_STATECLASS |  | Holding register 519/ | uint16 | R/W | alarmstate | 1
Holding reg 520 | HREG_ALARM20_YY |  | Holding register 520/ | uint16 | R/W | none | 1
Holding reg 521 | HREG_ALARM20_MM |  | Holding register 521/ | uint16 | R/W | none | 1
Holding reg 522 | HREG_ALARM20_DD |  | Holding register 522/ | uint16 | R/W | none | 1
Holding reg 523 | HREG_ALARM20_HH |  | Holding register 523/ | uint16 | R/W | none | 1
Holding reg 524 | HREG_ALARM20_MI |  | Holding register 524/ | uint16 | R/W | none | 1
Holding reg 538 | HREG_ALARM_SERVICE_TIME | Service reminder | Number of days until service reminder alarm is given | uint16 | R/W | value_as_days | 1
Holding reg 581 | HREG_N_O_ALARMS | Number of alarms | Current number of alarms in the alarm log | uint16 | R/W | none | 1
Holding reg 599 | HREG_SW_VERSION | ESC SW version | ESC Software release number | uint16 | R/W | none | 100
Holding reg 649 | HREG_CIRCULATION_MIN_FANSPEED | Circulation air fan min. speed | Minimum speed of the circulation air fan in constant or variable mode | uint16 | R/W | none | 1 | 20,100 | Kotilämpö, EMB and MixBox
Holding reg 650 | HREG_CIRCULATION_MAX_FANSPEED | Circulation air fan max. speed | Maximum speed of the circulation air fan in variable mode | uint16 | R/W | none | 1 | 20,100 | Kotilämpö, EMB and MixBox
Holding reg 676 | HREG_TC1_SP_AT_MINUS_20 | TC1 SP when TE01 is -20C | Supply air setpoint at outside temperature -20C, when using outside air temp compensated temp control | uint16 | R/W | none | 10
Holding reg 677 | HREG_TC1_SP_AT_ZERO | TC1 SP when TE01 is 0C | Supply air setpoint at outside temperature 0C, when using outside air temp compensated temp control | uint16 | R/W | none | 10
Holding reg 678 | HREG_TC1_SP_AT_PLUS_20 | TC1 SP when TE01 is +20C | Supply air setpoint at outside temperature +20C, when using outside air temp compensated temp control | uint16 | R/W | none | 10
Holding reg 703 | HREG_CIRCULATION_FANSPEED | Circulation air fan speed | Speed of the circulation air fan in constant mode | uint16 | R/W | none | 1 | 20,100 | Kotilämpö, EMB, Mixbox, and machines with closed circulation air (Pallas KI)
Holding reg 710 | HREG_DAYS_RUNNING |  | Number of days since service notification was acknowledged. | uint16 | R/W | none | 1
Holding reg 726 | HREG_MB_MEASUREMENT_UPD | Modbus update interval | Modbus measurement register update interval in seconds | uint16 | R/W | none | 1 | 1,60
Holding reg 733 | HREG_MODBUS_SPEED | Modbus speed | Modbus RTU serial line speed | enumeration | R/W | modbusspeed | 1
Holding reg 734 | HREG_MODBUS_PARITY | Modbus parity | Modbus RTU serial line parity | enumeration | R/W | modbusparity | 1
Holding reg 774 | HREG_EFFECTIVE_CIRCULATION | Fan speed, circulation air | Circulation air fan's current speed | uint16 | R | none | 1 |  | Kotilämpö, EMB, Mixbox
Holding reg 780 | HREG_AO1_VOLT | AO1 voltage | The voltage on Analog Output 1 | uint16 | R | none | 10
Holding reg 781 | HREG_AO2_VOLT | AO2 voltage | The voltage on Analog Output 2 | uint16 | R | none | 10
Holding reg 783 | HREG_AO4_VOLT | AO4 voltage | The voltage on Analog Output 4 | uint16 | R | none | 10
Holding reg 784 | HREG_AO5_VOLT | AO5 voltage | The voltage on Analog Output 5 | uint16 | R | none | 10
Holding reg 785 | HREG_AO6_VOLT | AO6 voltage | The voltage on Analog Output 6 | uint16 | R | none | 10
Holding reg 788 | HREG_DI9_PULSE_CNT | DI9 pulse count | Number of pulses detected on DI9 | uint16 | R | none | 1
Holding reg 789 | HREG_DI_BITMAP | DI1-12 and X9-GPIO1-3 status | Status bitmap of digital inputs DI1 to DI12 and GPIO pins 1-3 on connector X9 | uint16 | R | none | 1
Holding reg 798 | HREG_DO_BITMAP | DO1-8 status | Status bitmap of digital outputs (relays) | uint16 | R | none | 1

## Enumerators
Enumerators
Sub-type (ref) | Label | Value | Sub-type (ref) | Label | Value
Enumeration enabledisable |  |  | Enumeration alarmstate
| Disable | 0 |  | Off | 0
| Enable | 1 |  | Acked | 1
|  |  |  | On | 2
Enumeration allowdeny
| Deny | 0 | Enumeration mode
| Allow | 1 |  | Home | 0
|  |  |  | Max. cooling | 1
Enumeration onoff |  |  |  | Max. heating | 2
| Off | 0 |  | Alarm A | 4
| On | 1 |  | Stop | 8
|  |  |  | Away mode | 16
Enumeration analogIn |  |  |  | mode | 32
| No input | 0 |  | Temperature boost | 64
| CO₂ sensor 1 | 1 |  | CO₂ boosting | 128
| CO₂ sensor 2 | 2 |  | %RH boosting | 256
| CO₂ sensor 3 | 3 |  | Manual boost | 512
| %RH sensor 1 | 4 |  | Overpressure mode | 1024
| %RH sensor 2 | 5 |  | Cooker hood on | 2048
| %RH sensor 3 | 6 |  | Central vacuum cleaner on | 4096
| Ouside air temperature sensor | 7 |  | mode | 8192
| Room temperature sensor 1 | 8 |  | Summer night cooling | 16384
| Room temperature sensor 2 | 9 |  | Defrosting | 32768
| Room temperature sensor 3 | 10
| External deviation for temperature setpoint | 11 | Enumeration tempstep
| Constant supply air duct pressure sensor PDE10 | 15 |  | None | 0
| Constant extract air duct pressure sensor PDE30 | 16 |  | Cooling | 1
| Aqua water tank temperature TE80 | 131 |  | Heat recovery | 2
| Aqua cool water tank temperature TE70 | 132 |  | Heating | 4
| Aqua cool return water temperature from cooling load and tank TE71 | 133 |  | Summer night cooling | 6
| RH sensor for outside air humidity | 140 |  | Starting up | 7
| RH sensor for waste air humidity | 141 |  | Dehumidification | 8
Enumeration alarmtypes |  |  | Enumeration modbusspeed
| No alarm | 0 |  | 9600 | 1
| TE05 min | 1 |  | 19200 | 2
| TE10 min | 2 |  | 115200 | 3
| TE10 max | 3
| TE20 max | 4 | Enumeration modbusparity
| TE30 min | 5 |  | None | 1
| TE30 max | 6 |  | Even | 2
| Heat pump | 7
| EH-alarm | 8 | Enumeration miscconfbitfield
| TE45 min | 9 |  | TE31 temperature limitation with fixed limits (Pelican HP) | 2
| HRW | 10 |  | HP fan extended runtime (see reg. 161) | 4
| Cooling alarm (unused) | 11 |  | TE31 temperature limitation with PI controller (Pegasos/Pallas HP) | 8
| Emergency stop | 12 |  | On/off cascade controller function (Heating) | 16
| External alarm | 13 |  | MDX compressor effect limitation using TE62 | 64
| Service reminder | 14
| PDS10 | 15 | Enumeration escfanspeed
| Supply filter high | 16 |  | Fanspeed level 1 (Away-mode) | 1
| Extract filter high | 17 |  | Fanspeed level 2 (Home-mode) | 2
| Supply fan pressure | 20 |  | Fanspeed level 3 (Home-mode with high fan speeds) | 3
| Exhaust fan pressure | 21 |  | Fanspeed level 4 (Manual boost with timer) | 4
| TE30 max {50 ?} | 22
| TE52 H | 24
| Supply air pressure | 25
| Extract air pressure | 26
| TE02 H | 27
| Service reminder | 28
| TE49 L | 29