## Register list
eAir MD Modbus register list | 2018-05-04
Conforming to MD software versions 1.14 and later.
Protocol: Modbus RTU, RS485
Serial line default parameters: 19200 bps, 8 N 1
Serial line speed is configurable to 9600, 19200 or 115200 bps
Serial line parity is configurable to None or Even parity
Registers marked “reserved” must not be altered!
MODBUS HOLDING REGISTERS
Address | Symbol | Type | Multiplier | Bounds (raw value) | Name | Description | Title (en translation) | Help text (en translation) | Notes
hreg 0 | Reserved
Registers 1 to 49 are measurements and status information (read only)
hreg 1 | HREG_T_OP1 | int16 | 10 |  | Room temperature sensor TE20 | Temperature at operator panel 1 |  | Temperature at operator panel 1
hreg 2 | HREG_T_OP2 | int16 | 10 |  | Room temperature sensor TE21 | Temperature at operator panel 2 |  | Temperature at operator panel 2
hreg 3 | HREG_EFFECTIVE_TF | uint16 | 1 |  | Current supply fan speed | The current effective TF fanspeed | Fan speed, supply air | Current supply air fan speed
hreg 4 | HREG_EFFECTIVE_PF | uint16 | 1 |  | Current exhaust fan speed | The current effective PF fanspeed | Fan speed, extract air | Current extract air fan speed
hreg 5 | HREG_UPCOMING_TIME_PROGRAM | uint16 | 1 |  | Next time program | Indicates the time program which will start during the next two hours. |  |  | Values 1-20 indicate week program slots, value 101-105 indicate year program slots
hreg 6 | HREG_T_FRS | int16 | 10 |  | Fresh air | TE01 (fresh air) temperature. | Fresh air | Outside air temperature at the unit (sensor TE01)
hreg 7 | HREG_T_SPLY_LTO | int16 | 10 |  | Supply air after HRC | TE05: Fresh (incoming) air temperature after HRC. | Supply air after HRC | Supply air temperature after heat recovery (sensor TE05)
hreg 8 | HREG_T_SPLY | int16 | 10 |  | Supply air | TE10 Room supply air temperature | Supply air | Supply air temperature after supply air heater (sensor TE10)
hreg 9 | HREG_T_WST | int16 | 10 |  | Waste air | TE32 Waste air temperature | Exhaust air | Exhaust air temperature (sensor TE32)
hreg 10 | HREG_T_EXT | int16 | 10 |  | Room removed air | TE30 Room removed air temperature. | Extract air temperature | Extract air temperature from building at the unit (sensor TE30)
hreg 11 | HREG_T_EXT_LTO | int16 | 10 |  | Removed air before HRC | TE31 removed air before heat recycler. | Extract air before HRC | Extract air temperature after extract air coil before heat recovery in HP units (sensor TE31)
hreg 12 | HREG_T_WR | int16 | 10 |  | Return water | TE45 heater element return water temperature. | Return water | Return water temperature in supply air heater (sensor TE45)
hreg 13 | HREG_HUM_EXT | uint16 | 1 |  | Exhaust air humidity | RH30 measurement, removed air relative humidity | Air humidity | Extract air relative humidity \%RH at the unit (sensor RH30)
hreg 14 | HREG_PRES_SPLYF | uint16 | 1 |  | Pressure difference supply | Pressure difference over filter, TF side | Pressure difference supply | Pressure difference over filter, TF side
hreg 15 | HREG_PRES_EXTF | uint16 | 1 |  | Pressure difference ext | Pressure difference over filter, PF side | Pressure difference ext. | Pressure difference over filter, PF side
hreg 16 | HREG_TE07 | int16 | 10 |  | HP/MDX/Dehum supply air | Supply air temperature after dehumidification coil, or after heat pump coil in HP-E, HP-W, MDX-E and MDX-W units (sensor TE07)
hreg 17 | HREG_AI1 | uint16 | 10 |  | Analog input voltage | Raw conversion result for AI1 | Measured input voltage | Current measured input voltage
hreg 18 | HREG_AI2 | uint16 | 10 |  | Analog input voltage | Raw conversion result for AI2 | Measured input voltage | Current measured input voltage
hreg 19 | HREG_AI3 | uint16 | 10 |  | Analog input voltage | Raw conversion result for AI3 | Measured input voltage | Current measured input voltage
hreg 20 | HREG_AI4 | uint16 | 10 |  | Analog input voltage | Raw conversion result for AI4 | Measured input voltage | Current measured input voltage
hreg 21 | HREG_AI5 | uint16 | 10 |  | Analog input voltage | Raw conversion result for AI5 | Measured input voltage | Current measured input voltage
hreg 22 | HREG_AI6 | uint16 | 10 |  | Analog input voltage | Raw conversion result for AI6 | Measured input voltage | Current measured input voltage
hreg 23 | HREG_AI1_RES | uint16 | 1 |  | Calculated value | Calculated result for AI1 | Calculated value | Calculated result
hreg 24 | HREG_AI2_RES | uint16 | 1 |  | Calculated value | Calculated result for AI2 | Calculated value | Calculated result
hreg 25 | HREG_AI3_RES | uint16 | 1 |  | Calculated value | Calculated result for AI3 | Calculated value | Calculated result
hreg 26 | HREG_AI4_RES | uint16 | 1 |  | Calculated value | Calculated result for AI4 | Calculated value | Calculated result
hreg 27 | HREG_AI5_RES | uint16 | 1 |  | Calculated value | Calculated result for AI5 | Calculated value | Calculated result
hreg 28 | HREG_AI6_RES | uint16 | 1 |  | Calculated value | Calculated result for AI6 | Calculated value | Calculated result
hreg 29 | HREG_LTO_N_SPLY | uint16 | 1 |  | Heat recovery efficiency n supply | HRC efficiency ratio (supply side) | Heat recovery efficiency, supply air | Supply air temperature efficiency. Calculated from outside air-, supply air after heat recovery- and extract air temperature
hreg 30 | HREG_LTO_N_EXT | uint16 | 1 |  | Heat recovery efficiency n exhaust | HRC efficiency ratio (ext (removed air) side) | Heat recovery efficiency, exhaust air | Extract air temperature efficiency. Calculated from extract air-, exhaust air- and outside air temperature. In HP-units calculated from HRC extract air-, exhaust air- and outside air temperature
hreg 31 | HREG_NTC_X6 | int16 | 10 |  | Input X6 | Optional NTC-10 input X6 measurement
hreg 32 | HREG_NTC_X7 | int16 | 10 |  | Input X7 | Optional NTC-10 input X7 measurement
hreg 33 | HREG_ABS_HUM_CTRL_OUTPUT | int16 | 1 |  | Absolute humidity control output | -100...0% = dehumidifying, 0 = none, 0...100% = humidifying
hreg 34 | HREG_NWK_STATUS | bitfield | 1 |  | Network status | Ethernet block status |  |  | #define EMAC_STATUS_FAIL 0x0001 #define EMAC_STATUS_OK 0x0002 #define EMAC_STATUS_AUTONEG_COMPLETE 0x0004 #define EMAC_STATUS_AUTONEG_FAIL 0x0008 #define EMAC_STATUS_LINK_OK 0x0010 /* 0: no link, 1: link ok */ #define EMAC_STATUS_LINK_SPEED 0x0020 /* 0: 10 M, 1: 100M */ #define EMAC_STATUS_DUPLEX 0x0040 /* 0: half duplex, 1: full duplex */ #define EMAC_STATUS_INIT_ONGOING 0x0080
hreg 35 | HREG_RH_MEAN | uint16 | 1 |  | 48h air humidity average | Mean relative humidity, with 48 hour history, updated every hour. | Average air humidity, 48h | Extract air 48h mean relative humidity \%RH at the unit (sensor RH30). Updated every hour
hreg 36 | HREG_ABSHUM10 | uint16 | 10 |  | Supply air absolute humidity | Supply air absolute humidity, calculated from sensors TE10 and RH10, assuming normal atmospheric pressure.
hreg 37 | HREG_SEC_RTC | uint16 | 1 |  | s | RTC seconds. | s | RTC seconds
hreg 38 | HREG_MIN_RTC | uint16 | 1 |  | min | RTC minutes. | min | RTC minutes
hreg 39 | HREG_HOUR_RTC | uint16 | 1 |  | h | RTC hours, 24 hour format. | h | RTC hours, 24 hour format
hreg 40 | HREG_DAY_RTC | uint16 | 1 |  |  | RTC day-of-month |  | RTC day of month
hreg 41 | HREG_MONTH_RTC | uint16 | 1 |  |  | RTC month. |  | RTC month
hreg 42 | HREG_YEAR_RTC | uint16 | 1 |  |  | RTC year, exporessed in years since 2000. |  | RTC year, expressed in years since 2000
hreg 43 | Reserved
hreg 44 | HREG_MODE | bitfield | 1 |  | Status | The current mode of the machine, used to display information to the user. | Status | All current states of unit, eg. Home, Central vacuum cleaner, HP/EDX defrost etc. | Bit 0 indicates Max cooling mode, bit 1: max heating. Bit 2: Machine is stopped due to A alarm. Bit 3 indicates the machine has been stopped by request (ie. not due to alarm condition). Bit 4: indicates Away state. Bit 5 is reserved. Bit 6 indicates temperature boosting, bit 7 CO2 boosting, bit 8 RH boosting, bit 9 manual boosting. Bit 10 overpressure mode, bit 11 cooker hood mode, bit 12 central vacuum cleaner mode. Bit 13 indicates cool-off period of electrical heating coil. Bit 14 indicates summer night cooling mode. Bit 15 indicates heat recovery wheel defrosting mode. Value 0 indicates “normal” state, no special status is active.
hreg 45 | HREG_EXTMODE | bitfield | 1 |  | Temperature control step | Currently active temperature control step: Cooling, Heat recovery (LTO), or heating. | Temperature controller | Displays current state of temperature controller; cooling, heat recovery, heating or none. | Bits 0,1,2,3 have “enumerated” meaning: TEMP_STEP_NONE = 0, TEMP_STEP_COOLING = 1, TEMP_STEP_LTO = 2, TEMP_STEP_HEATING = 4, TEMP_STEP_STARTUP = 7, TEMP_STEP_DEHUMIDIFICATION = 8. Bit 15 indicates Aqua mode, bit 14 indicates pre-heating active, bit 13 indicates that HP compressor effect is being limited, bit 12 indicates defrosting state of the HP or MDX unit
hreg 46 | HREG_ROOM_TEMP | int16 | 10 |  | Room temperature average | TE20 room temperature, average value calculated from op panel sensors and room temperature transmitters. | Room temperature average | Room temperature (average temperature of sensors connected to OP wallmounts and AI temperature measurements if connected)
hreg 47 | HREG_CASCADE_SP | int16 | 10 |  | Setpoint for supply air | Setpoint for temperature controller responsible for maintaining the room supply air at a constant level | Setpoint for supply air | Setpoint for temperature controller responsible for maintaining the room supply air at a constant level
hreg 48 | HREG_DISPLAY_SP | int16 | 10 |  |  | Temperature controller setpoint shown to user
hreg 49 | HREG_OUTPUT | int16 | 1 |  | Controller output | Output from the TC1 temperature PI controller | Temperature controller output | -200 to -100 additional cooling, -100...-1=cooling, 0=nothing, 1...100=heat recovery, 101...200=additional heating or heat pump, 201...300=additional heating in heat pump units
hreg 50 | Reserved
hreg 51 | Reserved
hreg 52 | Reserved
hreg 53 | Reserved
hreg 54 | Reserved
hreg 55 | Reserved
hreg 56 | Reserved
hreg 57 | Reserved
hreg 58 | Reserved
hreg 59 | Reserved
hreg 60 | Reserved
hreg 61 | Reserved
hreg 62 | Reserved
hreg 63 | Reserved
hreg 64 | Reserved
hreg 65 | Reserved
hreg 66 | Reserved
hreg 67 | Reserved
hreg 68 | Reserved
hreg 69 | Reserved
hreg 70 | Reserved
hreg 71 | Reserved
hreg 72 | Reserved
hreg 73 | Reserved
hreg 74 | Reserved
hreg 75 | Reserved
hreg 76 | Reserved
hreg 77 | Reserved
hreg 78 | Reserved
hreg 79 | Reserved
hreg 80 | Reserved
hreg 81 | Reserved
hreg 82 | Reserved
hreg 83 | Reserved
hreg 84 | Reserved
hreg 85 | Reserved
hreg 86 | Reserved
hreg 87 | Reserved
hreg 88 | Reserved
hreg 89 | Reserved
hreg 90 | Reserved
hreg 91 | Reserved
hreg 92 | Reserved
hreg 93 | Reserved
hreg 94 | Reserved
hreg 95 | Reserved
hreg 96 | Reserved
hreg 97 | Reserved
hreg 98 | Reserved
hreg 99 | Reserved
hreg 100 | Reserved
hreg 101 | Reserved
hreg 102 | Reserved
hreg 103 | Reserved
hreg 104 | HREG_AI1_TYPE | uint16 | 1 |  | Sensor type | Type of external sensor in AI1. | Sensor type
hreg 105 | HREG_AI2_TYPE | uint16 | 1 |  | Sensor type | Type of external sensor in AI2. | Sensor type
hreg 106 | HREG_AI3_TYPE | uint16 | 1 |  | Sensor type | Type of external sensor in AI3. | Sensor type
hreg 107 | HREG_AI4_TYPE | uint16 | 1 |  | Sensor type | Type of external sensor in AI4. | Sensor type
hreg 108 | HREG_AI5_TYPE | uint16 | 1 |  | Sensor type | Type of external sensor in AI5. | Sensor type
hreg 109 | HREG_AI6_TYPE | uint16 | 1 |  | Sensor type | Type of external sensor in AI6. | Sensor type
hreg 110 | HREG_AI1_VL | uint16 | 10 | 0 - 100 | Voltage low | AI1 voltage low | Voltage low | Input signal lower limit
hreg 111 | HREG_AI2_VL | uint16 | 10 | 0 - 100 | Voltage low | AI2 voltage low | Voltage low | Input signal lower limit
hreg 112 | HREG_AI3_VL | uint16 | 10 | 0 - 100 | Voltage low | AI3 voltage low | Voltage low | Input signal lower limit
hreg 113 | HREG_AI4_VL | uint16 | 10 | 0 - 100 | Voltage low | AI4 voltage low | Voltage low | Input signal lower limit
hreg 114 | HREG_AI5_VL | uint16 | 10 | 0 - 100 | Voltage low | AI5 voltage low | Voltage low | Input signal lower limit
hreg 115 | HREG_AI6_VL | uint16 | 10 | 0 - 100 | Voltage low | AI6 voltage low | Voltage low | Input signal lower limit
hreg 116 | HREG_AI1_VH | uint16 | 10 | 0 - 100 | Voltage high | AI1 voltage high | Voltage high | Input signal upper limit
hreg 117 | HREG_AI2_VH | uint16 | 10 | 0 - 100 | Voltage high | AI2 voltage high | Voltage high | Input signal upper limit
hreg 118 | HREG_AI3_VH | uint16 | 10 | 0 - 100 | Voltage high | AI3 voltage high | Voltage high | Input signal upper limit
hreg 119 | HREG_AI4_VH | uint16 | 10 | 0 - 100 | Voltage high | AI4 voltage high | Voltage high | Input signal upper limit
hreg 120 | HREG_AI5_VH | uint16 | 10 | 0 - 100 | Voltage high | AI5 voltage high | Voltage high | Input signal upper limit
hreg 121 | HREG_AI6_VH | uint16 | 10 | 0 - 100 | Voltage high | AI6 voltage high | Voltage high | Input signal upper limit
hreg 122 | HREG_AI1_RL | int16 | 1 |  | Result low | AI1 output value from voltage low | Voltage low, effect | Result of input signal equivalent to Voltage low value
hreg 123 | HREG_AI2_RL | int16 | 1 |  | Result low | AI2 output value from voltage low | Voltage low, effect | Result of input signal equivalent to Voltage low value
hreg 124 | HREG_AI3_RL | int16 | 1 |  | Result low | AI3 output value from voltage low | Voltage low, effect | Result of input signal equivalent to Voltage low value
hreg 125 | HREG_AI4_RL | int16 | 1 |  | Result low | AI4 output value from voltage low | Voltage low, effect | Result of input signal equivalent to Voltage low value
hreg 126 | HREG_AI5_RL | int16 | 1 |  | Result low | AI5 output value from voltage low | Voltage low, effect | Result of input signal equivalent to Voltage low value
hreg 127 | HREG_AI6_RL | int16 | 1 |  | Result low | AI6 output value from voltage low | Voltage low, effect | Result of input signal equivalent to Voltage low value
hreg 128 | HREG_AI1_RH | int16 | 1 |  | Result high | AI1 output value from voltage high | Voltage high, effect | Result of input signal equivalent to Voltage high value
hreg 129 | HREG_AI2_RH | int16 | 1 |  | Result high | AI2 output value from voltage high | Voltage high, effect | Result of input signal equivalent to Voltage high value
hreg 130 | HREG_AI3_RH | int16 | 1 |  | Result high | AI3 output value from voltage high | Voltage high, effect | Result of input signal equivalent to Voltage high value
hreg 131 | HREG_AI4_RH | int16 | 1 |  | Result high | AI4 output value from voltage high | Voltage high, effect | Result of input signal equivalent to Voltage high value
hreg 132 | HREG_AI5_RH | int16 | 1 |  | Result high | AI5 output value from voltage high | Voltage high, effect | Result of input signal equivalent to Voltage high value
hreg 133 | HREG_AI6_RH | int16 | 1 |  | Result high | AI6 output value from voltage high | Voltage high, effect | Result of input signal equivalent to Voltage high value
hreg 134 | HREG_TE01_24H_AVG | int16 | 10 |  | Average outside temperature | 24-hour outside temperature average
hreg 135 | HREG_T_SETPOINT | int16 | 10 | 0 - 500 | Supply air setpoint | The desired setpoint set by the user. | Supply air setpoint | Desired setpoint set by the user
hreg 136 | Reserved
hreg 137 | HREG_TE01_SUMMER_WINTER_THRESHOLD | int16 | 10 | -100 - 150 | Summer/Winter threshold | Summer/Winter season 24-hour average outside temperature threshold value | Summer/winter threshold temperature | Outside air 24h average temperature; in summer mode extract air 48h average humidity, in winter mode a fixed \%RH threshold
hreg 138 | Reserved
hreg 139 | Reserved
hreg 140 | Reserved
hreg 141 | Reserved
hreg 142 | Reserved
hreg 143 | Reserved
hreg 144 | Reserved
hreg 145 | Reserved
hreg 146 | Reserved
hreg 147 | Reserved
hreg 148 | Reserved
hreg 149 | Reserved
hreg 150 | Reserved
hreg 151 | Reserved
hreg 152 | Reserved
hreg 153 | Reserved
hreg 154 | Reserved
hreg 155 | Reserved
hreg 156 | Reserved
hreg 157 | Reserved
hreg 158 | Reserved
hreg 159 | Reserved
hreg 160 | Reserved
hreg 161 | Reserved
hreg 162 | Reserved
hreg 163 | Reserved
hreg 164 | Reserved
hreg 165 | Reserved
hreg 166 | Reserved
hreg 167 | Reserved
hreg 168 | Reserved
hreg 169 | Reserved
hreg 170 | Reserved
hreg 171 | Reserved
hreg 172 | HREG_TEMP_DECREASE_VAL | int16 | 10 | 0 - 150 | Temperature decrease | The amount of degrees the temperature should be lowered then temperature decrease function is on. | Temperature decrease | Number of degrees, under which the temperature should be maintained when temperature decrease function is on | Low limit can be negative to enable temperature increase function.
hreg 173 | Reserved
hreg 174 | Reserved
hreg 175 | Reserved
hreg 176 | Reserved
hreg 177 | Reserved
hreg 178 | Reserved
hreg 179 | Reserved
hreg 180 | Reserved
hreg 181 | Reserved
hreg 182 | Reserved
hreg 183 | Reserved
hreg 184 | Reserved
hreg 185 | Reserved
hreg 186 | Reserved
hreg 187 | Reserved
hreg 188 | Reserved
hreg 189 | Reserved
hreg 190 | Reserved
hreg 191 | Reserved
hreg 192 | Reserved
hreg 193 | Reserved
hreg 194 | Reserved
hreg 195 | Reserved
hreg 196 | Reserved
hreg 197 | Reserved
hreg 198 | Reserved
hreg 199 | Reserved
hreg 200 | Reserved
hreg 201 | Reserved
hreg 202 | Reserved
hreg 203 | Reserved
hreg 204 | Reserved
hreg 205 | Reserved
hreg 206 | Reserved
hreg 207 | Reserved
hreg 208 | Reserved
hreg 209 | Reserved
hreg 210 | HREG_DAY_WC1 | bitfield | 1 |  | Week timer slot #1 | Days when allowed. | Days |  | Bit 0: Sunday … Bit 6: Saturday
hreg 211 | HREG_STA_HOUR_WC1 | uint16 | 1 |  |  | Start h | WC1 Start h | WC1 Start h
hreg 212 | HREG_STA_MIN_WC1 | uint16 | 1 |  |  | Start m | WC1 Start m | WC1 Start m
hreg 213 | HREG_STO_HOUR_WC1 | uint16 | 1 |  |  | Stop h | WC1 Stop h | WC1 Stop h
hreg 214 | HREG_STO_MIN_WC1 | uint16 | 1 |  |  | Stop m | WC1 Stop m | WC1 Stop m
hreg 215 | HREG_WC1 | enumeration | 1 |  |  | Function | WC1 Function | WC1 Function
hreg 216 | HREG_DAY_WC2 | bitfield | 1 |  | Week timer slot #2 | See description for register 210 | Days | Days | #define TIMER_PROGRAM_OFF 0 #define TIMER_AWAY 1 #define TIMER_AWAY_LONG 2 #define TIMER_HEAT_DIS 3 #define TIMER_COOL_DIS 4 #define TIMER_TEMP_DECR 5 #define TIMER_MAX_H 6 #define TIMER_MAX_C 7 #define TIMER_RELAY 16 #define TIMER_BOOST 17 /* Circulation air state change time program (Pallas) */ #define TIMER_CLOSED_CIRCULATION 18 /* This time program function is relevant in OFFICE program variant (use * method) and it means that the machine should be running (instead of * being in STOP state). */ #define TIMER_RUNTIME 30
hreg 217 | HREG_STA_HOUR_WC2 | uint16 | 1 |  |  | See description for register 211 | WC1 Start h | WC1 Start h
hreg 218 | HREG_STA_MIN_WC2 | uint16 | 1 |  |  | See description for register 212 | WC1 Start m | WC1 Start m
hreg 219 | HREG_STO_HOUR_WC2 | uint16 | 1 |  |  | See description for register 213 | WC1 Stop h | WC1 Stop h
hreg 220 | HREG_STO_MIN_WC2 | uint16 | 1 |  |  | See description for register 214 | WC1 Stop m | WC1 Stop m
hreg 221 | HREG_WC2 | enumeration | 1 |  |  | See description for register 215 | WC1 Function | WC1 Function
hreg 222 | HREG_DAY_WC3 | bitfield | 1 |  | Week timer slot #3 | See description for register 210 | Days | Days
hreg 223 | HREG_STA_HOUR_WC3 | uint16 | 1 |  |  | See description for register 211 | WC1 Start h | WC1 Start h
hreg 224 | HREG_STA_MIN_WC3 | uint16 | 1 |  |  | See description for register 212 | WC1 Start m | WC1 Start m
hreg 225 | HREG_STO_HOUR_WC3 | uint16 | 1 |  |  | See description for register 213 | WC1 Stop h
hreg 226 | HREG_STO_MIN_WC3 | uint16 | 1 |  |  | See description for register 214 | WC1 Stop m | WC1 Stop m
hreg 227 | HREG_WC3 | enumeration | 1 |  |  | See description for register 215 | WC1 Function | WC1 Function
hreg 228 | HREG_DAY_WC4 | bitfield | 1 |  | Week timer slot #4 | See description for register 210 | Days | Days
hreg 229 | HREG_STA_HOUR_WC4 | uint16 | 1 |  |  | See description for register 211 | WC1 Start h | WC1 Start h
hreg 230 | HREG_STA_MIN_WC4 | uint16 | 1 |  |  | See description for register 212 | WC1 Start m | WC1 Start m
hreg 231 | HREG_STO_HOUR_WC4 | uint16 | 1 |  |  | See description for register 213 | WC1 Stop h | WC1 Stop h
hreg 232 | HREG_STO_MIN_WC4 | uint16 | 1 |  |  | See description for register 214 | WC1 Stop m | WC1 Stop m
hreg 233 | HREG_WC4 | uint16 | 1 |  |  | See description for register 215
hreg 234 | HREG_DAY_WC5 | bitfield | 1 |  | Week timer slot #5 | See description for register 210 | Days | Days
hreg 235 | HREG_STA_HOUR_WC5 | uint16 | 1 |  |  | See description for register 211 | WC1 Start h | WC1 Start h
hreg 236 | HREG_STA_MIN_WC5 | uint16 | 1 |  |  | See description for register 212 | WC1 Start m | WC1 Start m
hreg 237 | HREG_STO_HOUR_WC5 | uint16 | 1 |  |  | See description for register 213 | WC1 Stop h | WC1 Stop h
hreg 238 | HREG_STO_MIN_WC5 | uint16 | 1 |  |  | See description for register 214 | WC1 Stop m | WC1 Stop m
hreg 239 | HREG_WC5 | uint16 | 1 |  |  | See description for register 215
hreg 240 | HREG_DAY_WC6 | bitfield | 1 |  | Week timer slot #6 | See description for register 210 | Days | Days
hreg 241 | HREG_STA_HOUR_WC6 | uint16 | 1 |  |  | See description for register 211 | WC1 Start h | WC1 Start h
hreg 242 | HREG_STA_MIN_WC6 | uint16 | 1 |  |  | See description for register 212
hreg 243 | HREG_STO_HOUR_WC6 | uint16 | 1 |  |  | See description for register 213
hreg 244 | HREG_STO_MIN_WC6 | uint16 | 1 |  |  | See description for register 214
hreg 245 | HREG_WC6 | uint16 | 1 |  |  | See description for register 215
hreg 246 | HREG_DAY_WC7 | bitfield | 1 |  | Week timer slot #7 | See description for register 210 | Days | Days
hreg 247 | HREG_STA_HOUR_WC7 | uint16 | 1 |  |  | See description for register 211 | WC1 Start h | WC1 Start h
hreg 248 | HREG_STA_MIN_WC7 | uint16 | 1 |  |  | See description for register 212
hreg 249 | HREG_STO_HOUR_WC7 | uint16 | 1 |  |  | See description for register 213
hreg 250 | HREG_STO_MIN_WC7 | uint16 | 1 |  |  | See description for register 214
hreg 251 | HREG_WC7 | uint16 | 1 | undefined |  | See description for register 215
hreg 252 | HREG_DAY_WC8 | bitfield | 1 |  | Week timer slot #8 | See description for register 210 | Days | Days
hreg 253 | HREG_STA_HOUR_WC8 | uint16 | 1 |  |  | See description for register 211 | WC1 Start h | WC1 Start h
hreg 254 | HREG_STA_MIN_WC8 | uint16 | 1 |  |  | See description for register 212
hreg 255 | HREG_STO_HOUR_WC8 | uint16 | 1 |  |  | See description for register 213
hreg 256 | HREG_STO_MIN_WC8 | uint16 | 1 |  |  | See description for register 214
hreg 257 | HREG_WC8 | uint16 | 1 | undefined |  | See description for register 215
hreg 258 | HREG_DAY_WC9 | bitfield | 1 |  | Week timer slot #9 | See description for register 210 | Days | Days
hreg 259 | HREG_STA_HOUR_WC9 | uint16 | 1 |  |  | See description for register 211
hreg 260 | HREG_STA_MIN_WC9 | uint16 | 1 |  |  | See description for register 212
hreg 261 | HREG_STO_HOUR_WC9 | uint16 | 1 |  |  | See description for register 213
hreg 262 | HREG_STO_MIN_WC9 | uint16 | 1 |  |  | See description for register 214
hreg 263 | HREG_WC9 | uint16 | 1 |  |  | See description for register 215
hreg 264 | HREG_DAY_WC10 | bitfield | 1 |  | Week timer slot #10 | See description for register 210 | Days | Days
hreg 265 | HREG_STA_HOUR_WC10 | uint16 | 1 |  |  | See description for register 211
hreg 266 | HREG_STA_MIN_WC10 | uint16 | 1 |  |  | See description for register 212
hreg 267 | HREG_STO_HOUR_WC10 | uint16 | 1 |  |  | See description for register 213
hreg 268 | HREG_STO_MIN_WC10 | uint16 | 1 |  |  | See description for register 214
hreg 269 | HREG_WC10 | uint16 | 1 |  |  | See description for register 215
hreg 270 | HREG_DAY_WC11 | bitfield | 1 |  | Week timer slot #11 | See description for register 210 | Days | Days
hreg 271 | HREG_STA_HOUR_WC11 | uint16 | 1 |  |  | See description for register 211
hreg 272 | HREG_STA_MIN_WC11 | uint16 | 1 |  |  | See description for register 212
hreg 273 | HREG_STO_HOUR_WC11 | uint16 | 1 |  |  | See description for register 213
hreg 274 | HREG_STO_MIN_WC11 | uint16 | 1 |  |  | See description for register 214
hreg 275 | HREG_WC11 | uint16 | 1 |  |  | See description for register 215
hreg 276 | HREG_DAY_WC12 | bitfield | 1 |  | Week timer slot #12 | See description for register 210 | Days | Days
hreg 277 | HREG_STA_HOUR_WC12 | uint16 | 1 |  |  | See description for register 211
hreg 278 | HREG_STA_MIN_WC12 | uint16 | 1 |  |  | See description for register 212
hreg 279 | HREG_STO_HOUR_WC12 | uint16 | 1 |  |  | See description for register 213
hreg 280 | HREG_STO_MIN_WC12 | uint16 | 1 |  |  | See description for register 214
hreg 281 | HREG_WC12 | uint16 | 1 |  |  | See description for register 215
hreg 282 | HREG_DAY_WC13 | bitfield | 1 |  | Week timer slot #13 | See description for register 210 | Days | Days
hreg 283 | HREG_STA_HOUR_WC13 | uint16 | 1 |  |  | See description for register 211
hreg 284 | HREG_STA_MIN_WC13 | uint16 | 1 |  |  | See description for register 212
hreg 285 | HREG_STO_HOUR_WC13 | uint16 | 1 |  |  | See description for register 213
hreg 286 | HREG_STO_MIN_WC13 | uint16 | 1 |  |  | See description for register 214
hreg 287 | HREG_WC13 | uint16 | 1 |  |  | See description for register 215
hreg 288 | HREG_DAY_WC14 | bitfield | 1 |  | Week timer slot #14 | See description for register 210 | Days | Days
hreg 289 | HREG_STA_HOUR_WC14 | uint16 | 1 |  |  | See description for register 211
hreg 290 | HREG_STA_MIN_WC14 | uint16 | 1 |  |  | See description for register 212
hreg 291 | HREG_STO_HOUR_WC14 | uint16 | 1 |  |  | See description for register 213
hreg 292 | HREG_STO_MIN_WC14 | uint16 | 1 |  |  | See description for register 214
hreg 293 | HREG_WC14 | uint16 | 1 |  |  | See description for register 215
hreg 294 | HREG_DAY_WC15 | bitfield | 1 |  | Week timer slot #15 | See description for register 210 | Days | Days
hreg 295 | HREG_STA_HOUR_WC15 | uint16 | 1 |  |  | See description for register 211
hreg 296 | HREG_STA_MIN_WC15 | uint16 | 1 |  |  | See description for register 212
hreg 297 | HREG_STO_HOUR_WC15 | uint16 | 1 |  |  | See description for register 213
hreg 298 | HREG_STO_MIN_WC15 | uint16 | 1 |  |  | See description for register 214
hreg 299 | HREG_WC15 | uint16 | 1 |  |  | See description for register 215
hreg 300 | HREG_DAY_WC16 | bitfield | 1 |  | Week timer slot #16 | See description for register 210 | Days | Days
hreg 301 | HREG_STA_HOUR_WC16 | uint16 | 1 |  |  | See description for register 211
hreg 302 | HREG_STA_MIN_WC16 | uint16 | 1 |  |  | See description for register 212
hreg 303 | HREG_STO_HOUR_WC16 | uint16 | 1 |  |  | See description for register 213
hreg 304 | HREG_STO_MIN_WC16 | uint16 | 1 |  |  | See description for register 214
hreg 305 | HREG_WC16 | uint16 | 1 |  |  | See description for register 215
hreg 306 | HREG_DAY_WC17 | bitfield | 1 |  | Week timer slot #17 | See description for register 210 | Days | Days
hreg 307 | HREG_STA_HOUR_WC17 | uint16 | 1 |  |  | See description for register 211
hreg 308 | HREG_STA_MIN_WC17 | uint16 | 1 |  |  | See description for register 212
hreg 309 | HREG_STO_HOUR_WC17 | uint16 | 1 |  |  | See description for register 213
hreg 310 | HREG_STO_MIN_WC17 | uint16 | 1 |  |  | See description for register 214
hreg 311 | HREG_WC17 | uint16 | 1 |  |  | See description for register 215
hreg 312 | HREG_DAY_WC18 | bitfield | 1 |  | Week timer slot #18 | See description for register 210 | Days | Days
hreg 313 | HREG_STA_HOUR_WC18 | uint16 | 1 |  |  | See description for register 211
hreg 314 | HREG_STA_MIN_WC18 | uint16 | 1 |  |  | See description for register 212
hreg 315 | HREG_STO_HOUR_WC18 | uint16 | 1 |  |  | See description for register 213
hreg 316 | HREG_STO_MIN_WC18 | uint16 | 1 |  |  | See description for register 214
hreg 317 | HREG_WC18 | uint16 | 1 |  |  | See description for register 215
hreg 318 | HREG_DAY_WC19 | bitfield | 1 |  | Week timer slot #19 | See description for register 210 | Days | Days
hreg 319 | HREG_STA_HOUR_WC19 | uint16 | 1 |  |  | See description for register 211
hreg 320 | HREG_STA_MIN_WC19 | uint16 | 1 |  |  | See description for register 212
hreg 321 | HREG_STO_HOUR_WC19 | uint16 | 1 |  |  | See description for register 213
hreg 322 | HREG_STO_MIN_WC19 | uint16 | 1 |  |  | See description for register 214
hreg 323 | HREG_WC19 | uint16 | 1 |  |  | See description for register 215
hreg 324 | HREG_DAY_WC20 | bitfield | 1 |  | Week timer slot #20 | See description for register 210 | Days | Days
hreg 325 | HREG_STA_HOUR_WC20 | uint16 | 1 |  |  | See description for register 211
hreg 326 | HREG_STA_MIN_WC20 | uint16 | 1 |  |  | See description for register 212
hreg 327 | HREG_STO_HOUR_WC20 | uint16 | 1 |  |  | See description for register 213
hreg 328 | HREG_STO_MIN_WC20 | uint16 | 1 |  |  | See description for register 214
hreg 329 | HREG_WC20 | uint16 | 1 |  |  | See description for register 215
hreg 330 | HREG_STA_PV_Y1 | uint16 | 1 |  | Year timer slot #1 | Year program 1 start day-of-month
hreg 331 | HREG_STA_KK_Y1 | uint16 | 1 |  |  | Year program 1 stop month
hreg 332 | HREG_ACTIVE_TIMEPROGRAMS_1 | uint16 | 1 |  | Active time programs, week slots 1-16
hreg 333 | HREG_STA_HOUR_Y1 | uint16 | 1 |  |  | Year program 1 start hour
hreg 334 | HREG_STA_MIN_Y1 | uint16 | 1 |  |  | Year program 1 start minute
hreg 335 | HREG_STO_PV_Y1 | uint16 | 1 |  |  | Year program 1 stop day of month
hreg 336 | HREG_STO_KK_Y1 | uint16 | 1 |  |  | Year program 1 stop month
hreg 337 | HREG_ACTIVE_TIMEPROGRAMS_2 | uint16 | 1 |  | Active time programs, week slots 17-20 and year slots 1-5
hreg 338 | HREG_STO_HOUR_Y1 | uint16 | 1 |  |  | Year program 1 stop hour
hreg 339 | HREG_STO_MIN_Y1 | uint16 | 1 |  |  | Year program 1 stop minute
hreg 340 | HREG_Y1 | uint16 | 1 |  |  | Year program 1 action |  |  | #define TIMER_PROGRAM_OFF 0 #define TIMER_AWAY 1 #define TIMER_AWAY_LONG 2 #define TIMER_HEAT_DIS 3 #define TIMER_COOL_DIS 4 #define TIMER_TEMP_DECR 5 #define TIMER_MAX_H 6 #define TIMER_MAX_C 7 #define TIMER_RELAY 16 #define TIMER_BOOST 17 /* Circulation air state change time program (Pallas) */ #define TIMER_CLOSED_CIRCULATION 18 /* This time program function is relevant in OFFICE program variant (use * method) and it means that the machine should be running (instead of * being in STOP state). */ #define TIMER_RUNTIME 30
hreg 341 | HREG_STA_PV_Y2 | uint16 | 1 |  | Year timer slot #2 | See description for year program slot #1
hreg 342 | HREG_STA_KK_Y2 | uint16 | 1 |  |  | See description for year program slot #1
hreg 343 | HREG_UPTIME | uint16 | 1 |  | System uptime | Number of minutes since system was started. Note: count will reset to zero after approximately 45 days |  |  | Warning: the count is approximative, it should not be used for time-keeping purposes
hreg 344 | HREG_STA_HOUR_Y2 | uint16 | 1 |  |  | See description for year program slot #1
hreg 345 | HREG_STA_MIN_Y2 | uint16 | 1 |  |  | See description for year program slot #1
hreg 346 | HREG_STO_PV_Y2 | uint16 | 1 |  |  | See description for year program slot #1
hreg 347 | HREG_STO_KK_Y2 | uint16 | 1 |  |  | See description for year program slot #1
hreg 348 | Reserved | uint16 | 1 |  | Number of active panel bus units | The number of modbus slaves detected, updated every minute
hreg 349 | HREG_STO_HOUR_Y2 | uint16 | 1 |  |  | See description for year program slot #1
hreg 350 | HREG_STO_MIN_Y2 | uint16 | 1 |  |  | See description for year program slot #1
hreg 351 | HREG_Y2 | uint16 | 1 |  |  | See description for year program slot #1
hreg 352 | HREG_STA_PV_Y3 | uint16 | 1 |  | Year timer slot #3 | See description for year program slot #1
hreg 353 | HREG_STA_KK_Y3 | uint16 | 1 |  |  | See description for year program slot #1
hreg 354 | HREG_BOOTLOADER_VERSION | uint16 | 1 |  | Bootloader version | Bootloader version (desc.)
hreg 355 | HREG_STA_HOUR_Y3 | uint16 | 1 |  |  | See description for year program slot #1
hreg 356 | HREG_STA_MIN_Y3 | uint16 | 1 |  |  | See description for year program slot #1
hreg 357 | HREG_STO_PV_Y3 | uint16 | 1 |  |  | See description for year program slot #1
hreg 358 | HREG_STO_KK_Y3 | uint16 | 1 |  |  | See description for year program slot #1
hreg 359 | HREG_FILTER_TEST_HR | uint16 | 1 |  | Filter test hour | Filter test will begin at this hour (HH:00)
hreg 360 | HREG_STO_HOUR_Y3 | uint16 | 1 |  |  | See description for year program slot #1
hreg 361 | HREG_STO_MIN_Y3 | uint16 | 1 |  |  | See description for year program slot #1
hreg 362 | HREG_Y3 | uint16 | 1 |  |  | See description for year program slot #1
hreg 363 | HREG_STA_PV_Y4 | uint16 | 1 |  | Year timer slot #4 | See description for year program slot #1
hreg 364 | HREG_STA_KK_Y4 | uint16 | 1 |  |  | See description for year program slot #1
hreg 365 | HREG_FILTER_TEST_DAYS | uint16 | 1 |  | Filter test day-of-week | Filter test run on selected day on the selected hour |  |  | Expressed as a bitfield similar to week time programs
hreg 366 | HREG_STA_HOUR_Y4 | uint16 | 1 |  |  | See description for year program slot #1
hreg 367 | HREG_STA_MIN_Y4 | uint16 | 1 |  |  | See description for year program slot #1
hreg 368 | HREG_STO_PV_Y4 | uint16 | 1 |  |  | See description for year program slot #1
hreg 369 | HREG_STO_KK_Y4 | uint16 | 1 |  |  | See description for year program slot #1
hreg 370 | HREG_FILTER_TEST_TF | uint16 | 1 |  | Filter test TF fan speed | Filter test TF fan speed (desc.) |  |  | During filter test mode TF will run at this constant fanspeed even in constant duct pressure mode. Note that if value is outside range 20-100, 100% will be used
hreg 371 | HREG_STO_HOUR_Y4 | uint16 | 1 |  |  | See description for year program slot #1
hreg 372 | HREG_STO_MIN_Y4 | uint16 | 1 |  |  | See description for year program slot #1
hreg 373 | HREG_Y4 | uint16 | 1 |  |  | See description for year program slot #1
hreg 374 | HREG_STA_PV_Y5 | uint16 | 1 |  | Year timer slot #5 | See description for year program slot #1
hreg 375 | HREG_STA_KK_Y5 | uint16 | 1 |  |  | See description for year program slot #1
hreg 376 | HREG_FILTER_TEST_PF | uint16 | 1 |  | Filter test PF fan speed | Filter test PF fan speed (desc.) |  |  | During filter test mode PF will run at this constant fanspeed even in constant duct pressure mode. Note that if value is outside range 20-100, 100% will be used
hreg 377 | HREG_STA_HOUR_Y5 | uint16 | 1 |  |  | See description for year program slot #1
hreg 378 | HREG_STA_MIN_Y5 | uint16 | 1 |  |  | See description for year program slot #1
hreg 379 | HREG_STO_PV_Y5 | uint16 | 1 |  |  | See description for year program slot #1
hreg 380 | HREG_STO_KK_Y5 | uint16 | 1 |  |  | See description for year program slot #1
hreg 381 | Reserved
hreg 382 | HREG_STO_HOUR_Y5 | uint16 | 1 |  |  | See description for year program slot #1
hreg 383 | HREG_STO_MIN_Y5 | uint16 | 1 |  |  | See description for year program slot #1
hreg 384 | HREG_Y5 | uint16 | 1 |  |  | See description for year program slot #1
hreg 385 | HREG_ALARM1_ALMTYPE | uint16 | 1 |  | Alarm log entry #1 | Alarm 1 (newest) alarm type |  | Alarm 1 (newest) alarm type | ALARM_TE05_L = 1, ALARM_TE10_L = 2, ALARM_TE10_H = 3, ALARM_TE20_H = 4, ALARM_TE30_L = 5, ALARM_TE30_H = 6, ALARM_HP = 7, /* This is both HP and MDX */ ALARM_SLP = 8, ALARM_TE45_L = 9, ALARM_LTO = 10, ALARM_COOL = 11, ALARM_EMERGENCY_STOP = 12 , ALARM_EXTERNAL = 13, /** This used to be ALARM_FIRE on EDA */ ALARM_SERVICE =14 , ALARM_PDS10 = 15, ALARM_SPLY_FILT_H = 16, ALARM_EXT_FILT_H = 17, ALARM_SPLY_FILT_L = 18 , /* This alarm is actually not in use. It is relevant only for large machines with 2-speed fan control */ ALARM_EXT_FILT_L = 19 , /* This alarm is actually not in use. It is relevant only for large machines with 2-speed fan control */ ALARM_TF_PRES = 20, ALARM_PF_PRES = 21 , ALARM_TE50_H = 22, ALARM_TE52_H = 24, ALARM_TF_ROTATION = 25, ALARM_PF_ROTATION = 26, ALARM_TE02_H = 27, ALARM_SERVICE_CONSTANT_DUCT_PRES = 28, /* Under constant duct pressure control, Service alarm is triggered then fanspeeds reach a defined limit */
hreg 386 | HREG_ALARM1_STATECLASS | uint16 | 1 |  |  | This defines the status (low byte) of the alarm |  |  | ALARM_STATE_OFF = 0, ALARM_STATE_ACKED = 1, ALARM_STATE_ON = 2. Write “1” or “2” to this register to acknowledge the alarm.
hreg 387 | HREG_ALARM1_YY | uint16 | 1 |  |  | Alarm year
hreg 388 | HREG_ALARM1_MM | uint16 | 1 |  |  | Alarm month
hreg 389 | HREG_ALARM1_DD | uint16 | 1 |  |  | Alarm day.
hreg 390 | HREG_ALARM1_HH | uint16 | 1 |  |  | Alarm hour
hreg 391 | HREG_ALARM1_MI | uint16 | 1 |  |  | Alarm minutes
hreg 392 | HREG_ALARM2_ALMTYPE | uint16 | 1 |  | Alarm log entry #2 | See description for alarm log entry #1
hreg 393 | HREG_ALARM2_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 394 | HREG_ALARM2_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 395 | HREG_ALARM2_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 396 | HREG_ALARM2_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 397 | HREG_ALARM2_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 398 | HREG_ALARM2_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 399 | HREG_ALARM3_ALMTYPE | uint16 | 1 |  | Alarm log entry #3 | See description for alarm log entry #1
hreg 400 | HREG_ALARM3_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 401 | HREG_ALARM3_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 402 | HREG_ALARM3_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 403 | HREG_ALARM3_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 404 | HREG_ALARM3_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 405 | HREG_ALARM3_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 406 | HREG_ALARM4_ALMTYPE | uint16 | 1 |  | Alarm log entry #4 | See description for alarm log entry #1
hreg 407 | HREG_ALARM4_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 408 | HREG_ALARM4_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 409 | HREG_ALARM4_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 410 | HREG_ALARM4_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 411 | HREG_ALARM4_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 412 | HREG_ALARM4_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 413 | HREG_ALARM5_ALMTYPE | uint16 | 1 |  | Alarm log entry #5 | See description for alarm log entry #1
hreg 414 | HREG_ALARM5_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 415 | HREG_ALARM5_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 416 | HREG_ALARM5_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 417 | HREG_ALARM5_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 418 | HREG_ALARM5_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 419 | HREG_ALARM5_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 420 | HREG_ALARM6_ALMTYPE | uint16 | 1 |  | Alarm log entry #6 | See description for alarm log entry #1
hreg 421 | HREG_ALARM6_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 422 | HREG_ALARM6_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 423 | HREG_ALARM6_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 424 | HREG_ALARM6_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 425 | HREG_ALARM6_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 426 | HREG_ALARM6_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 427 | HREG_ALARM7_ALMTYPE | uint16 | 1 |  | Alarm log entry #7 | See description for alarm log entry #1
hreg 428 | HREG_ALARM7_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 429 | HREG_ALARM7_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 430 | HREG_ALARM7_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 431 | HREG_ALARM7_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 432 | HREG_ALARM7_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 433 | HREG_ALARM7_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 434 | HREG_ALARM8_ALMTYPE | uint16 | 1 |  | Alarm log entry #8 | See description for alarm log entry #1
hreg 435 | HREG_ALARM8_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 436 | HREG_ALARM8_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 437 | HREG_ALARM8_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 438 | HREG_ALARM8_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 439 | HREG_ALARM8_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 440 | HREG_ALARM8_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 441 | HREG_ALARM9_ALMTYPE | uint16 | 1 |  | Alarm log entry #9 | See description for alarm log entry #1
hreg 442 | HREG_ALARM9_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 443 | HREG_ALARM9_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 444 | HREG_ALARM9_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 445 | HREG_ALARM9_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 446 | HREG_ALARM9_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 447 | HREG_ALARM9_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 448 | HREG_ALARM10_ALMTYPE | uint16 | 1 |  | Alarm log entry #10 | See description for alarm log entry #1
hreg 449 | HREG_ALARM10_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 450 | HREG_ALARM10_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 451 | HREG_ALARM10_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 452 | HREG_ALARM10_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 453 | HREG_ALARM10_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 454 | HREG_ALARM10_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 455 | HREG_ALARM11_ALMTYPE | uint16 | 1 |  | Alarm log entry #11 | See description for alarm log entry #1
hreg 456 | HREG_ALARM11_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 457 | HREG_ALARM11_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 458 | HREG_ALARM11_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 459 | HREG_ALARM11_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 460 | HREG_ALARM11_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 461 | HREG_ALARM11_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 462 | HREG_ALARM12_ALMTYPE | uint16 | 1 |  | Alarm log entry #12 | See description for alarm log entry #1
hreg 463 | HREG_ALARM12_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 464 | HREG_ALARM12_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 465 | HREG_ALARM12_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 466 | HREG_ALARM12_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 467 | HREG_ALARM12_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 468 | HREG_ALARM12_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 469 | HREG_ALARM13_ALMTYPE | uint16 | 1 |  | Alarm log entry #13 | See description for alarm log entry #1
hreg 470 | HREG_ALARM13_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 471 | HREG_ALARM13_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 472 | HREG_ALARM13_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 473 | HREG_ALARM13_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 474 | HREG_ALARM13_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 475 | HREG_ALARM13_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 476 | HREG_ALARM14_ALMTYPE | uint16 | 1 |  | Alarm log entry #14 | See description for alarm log entry #1
hreg 477 | HREG_ALARM14_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 478 | HREG_ALARM14_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 479 | HREG_ALARM14_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 480 | HREG_ALARM14_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 481 | HREG_ALARM14_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 482 | HREG_ALARM14_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 483 | HREG_ALARM15_ALMTYPE | uint16 | 1 |  | Alarm log entry #15 | See description for alarm log entry #1
hreg 484 | HREG_ALARM15_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 485 | HREG_ALARM15_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 486 | HREG_ALARM15_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 487 | HREG_ALARM15_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 488 | HREG_ALARM15_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 489 | HREG_ALARM15_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 490 | HREG_ALARM16_ALMTYPE | uint16 | 1 |  | Alarm log entry #16 | See description for alarm log entry #1
hreg 491 | HREG_ALARM16_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 492 | HREG_ALARM16_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 493 | HREG_ALARM16_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 494 | HREG_ALARM16_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 495 | HREG_ALARM16_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 496 | HREG_ALARM16_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 497 | HREG_ALARM17_ALMTYPE | uint16 | 1 |  | Alarm log entry #17 | See description for alarm log entry #1
hreg 498 | HREG_ALARM17_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 499 | HREG_ALARM17_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 500 | HREG_ALARM17_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 501 | HREG_ALARM17_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 502 | HREG_ALARM17_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 503 | HREG_ALARM17_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 504 | HREG_ALARM18_ALMTYPE | uint16 | 1 |  | Alarm log entry #18 | See description for alarm log entry #1
hreg 505 | HREG_ALARM18_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 506 | HREG_ALARM18_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 507 | HREG_ALARM18_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 508 | HREG_ALARM18_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 509 | HREG_ALARM18_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 510 | HREG_ALARM18_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 511 | HREG_ALARM19_ALMTYPE | uint16 | 1 |  | Alarm log entry #19 | See description for alarm log entry #1
hreg 512 | HREG_ALARM19_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 513 | HREG_ALARM19_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 514 | HREG_ALARM19_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 515 | HREG_ALARM19_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 516 | HREG_ALARM19_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 517 | HREG_ALARM19_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 518 | HREG_ALARM20_ALMTYPE | uint16 | 1 |  | Alarm log entry #20 | See description for alarm log entry #1
hreg 519 | HREG_ALARM20_STATECLASS | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 520 | HREG_ALARM20_YY | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 521 | HREG_ALARM20_MM | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 522 | HREG_ALARM20_DD | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 523 | HREG_ALARM20_HH | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 524 | HREG_ALARM20_MI | uint16 | 1 |  |  | See description for alarm log entry #1
hreg 525 | Reserved
hreg 526 | Reserved
hreg 527 | Reserved
hreg 528 | Reserved
hreg 529 | Reserved
hreg 530 | Reserved
hreg 531 | Reserved
hreg 532 | Reserved
hreg 533 | Reserved
hreg 534 | Reserved
hreg 535 | Reserved
hreg 536 | Reserved
hreg 537 | Reserved
hreg 538 | HREG_ALARM_SERVICE_TIME | uint16 | 1 |  | Service reminder | Number of days until service reminder alarm is signaled. | Service reminder | Number of days until service reminder alarm is given
hreg 539 | Reserved
hreg 540 | Reserved
hreg 541 | Reserved
hreg 542 | Reserved
hreg 543 | Reserved
hreg 544 | Reserved
hreg 545 | Reserved
hreg 546 | Reserved
hreg 547 | Reserved
hreg 548 | Reserved
hreg 549 | Reserved
hreg 550 | Reserved
hreg 551 | Reserved
hreg 552 | Reserved
hreg 553 | Reserved
hreg 554 | Reserved
hreg 555 | Reserved
hreg 556 | Reserved
hreg 557 | Reserved
hreg 558 | Reserved
hreg 559 | Reserved
hreg 560 | Reserved
hreg 561 | Reserved
hreg 562 | Reserved
hreg 563 | Reserved
hreg 564 | Reserved
hreg 565 | Reserved
hreg 566 | Reserved
hreg 567 | Reserved
hreg 568 | Reserved
hreg 569 | Reserved
hreg 570 | Reserved
hreg 571 | Reserved
hreg 572 | Reserved
hreg 573 | Reserved
hreg 574 | Reserved
hreg 575 | Reserved
hreg 576 | Reserved
hreg 577 | Reserved
hreg 578 | HREG_B_ALARM_START | uint16 | 1 |  | Start time | B alarm relay signaling allowed start hour. | Start time | Allowed start time for B alarm output | The defined time is HH:00, where HH is the register's value
hreg 579 | HREG_B_ALARM_STOP | uint16 | 1 |  | Ending time | B alarm relay signaling allowed stop hour. | Ending time | Allowed stop time for B alarm output | The defined time is HH:00, where HH is the register's value
hreg 580 | HREG_B_ALARM_WEEKDAYS | bitfield | 1 |  | Weekdays | B alarm relay signaling allowed weekdays (bitmap, stored in low 7 bits of the register). | Weekdays | Choose allowed weekdays for B alarm output | Bit 0: Sunday … Bit 6: Saturday
hreg 581 | HREG_N_O_ALARMS | uint16 | 1 |  | Number of alarms | Current number of alarms in the alarm log. | Number of alarms | Current number of alarms in the alarm log
hreg 582 | HREG_C_MIN_RTC | uint16 | 1 |  |  | RTC interface for changing minutes field
hreg 583 | HREG_C_HOUR_RTC | uint16 | 1 |  |  | RTC interface for changing hour field
hreg 584 | HREG_C_DAY_RTC | uint16 | 1 |  |  | RTC interface for changing day of month field
hreg 585 | HREG_C_MONTH_RTC | uint16 | 1 |  |  | RTC interface for changing month field
hreg 586 | HREG_C_YEAR_RTC | uint16 | 1 |  |  | RTC interface for changing year field
hreg 587 | Reserved
hreg 588 | Reserved
hreg 589 | Reserved
hreg 590 | Reserved
hreg 591 | Reserved
hreg 592 | Reserved
hreg 593 | Reserved
hreg 594 | Reserved
hreg 595 | Reserved
hreg 596 | Reserved
hreg 597 | HREG_FAMILY_TYPE | uint16 | 1 |  | Family | Machine family type | Family | Machine family type
hreg 598 | HREG_HW_VERSION | enumeration | 1 |  | Hardware version | Hardware version desc | MD Hardware version | Unit motherboard hardware version | Value 1 corresponds to Rev.A, value 2 is B, value is C and so forth up to 27 which is Rev.Z
hreg 599 | HREG_SW_VERSION | uint16 | 100 |  | MD SW version | MD Software release number | MD SW version | Unit motherboard software version
hreg 600 | Reserved
hreg 601 | Reserved
hreg 602 | Reserved
hreg 603 | Reserved
hreg 604 | Reserved
hreg 605 | Reserved
hreg 606 | Reserved
hreg 607 | Reserved
hreg 608 | Reserved
hreg 609 | Reserved
hreg 610 | Reserved
hreg 611 | Reserved
hreg 612 | Reserved
hreg 613 | Reserved
hreg 614 | Reserved
hreg 615 | Reserved
hreg 616 | Reserved
hreg 617 | Reserved
hreg 618 | Reserved
hreg 619 | Reserved
hreg 620 | Reserved
hreg 621 | Reserved
hreg 622 | Reserved
hreg 623 | Reserved
hreg 624 | Reserved
hreg 625 | Reserved
hreg 626 | Reserved
hreg 627 | Reserved
hreg 628 | Reserved
hreg 629 | Reserved
hreg 630 | Reserved
hreg 631 | Reserved
hreg 632 | Reserved
hreg 633 | Reserved
hreg 634 | Reserved
hreg 635 | Reserved
hreg 636 | Reserved
hreg 637 | Reserved
hreg 638 | Reserved
hreg 639 | Reserved
hreg 640 | HREG_MBADDR | uint16 | 1 | 1 - 100 | Modbus id | Modbus address used by the card. | Modbus id | MD card modbus address 1 - 100
hreg 641 | Reserved
hreg 642 | Reserved
hreg 643 | Reserved
hreg 644 | Reserved
hreg 645 | Reserved
hreg 646 | Reserved
hreg 647 | Reserved
hreg 648 | Reserved
hreg 649 | Reserved
hreg 650 | Reserved
hreg 651 | Reserved
hreg 652 | Reserved
hreg 653 | Reserved
hreg 654 | HREG_IPADDR_HIGH | uint16 | 1 |  | IP address | IP address high bytes Useful values: 192.168 would be 49320 | IP address |  | Calculate this as A*2^8+B for IP addr starting with bytes A.B
hreg 655 | HREG_IPADDR_LOW | uint16 | 1 |  | IP address | IP address low bytes | IP address |  | : Calculate this as C*2^8+D for IP addr ending with bytes C.D
hreg 656 | HREG_GWIPADDR_HIGH | uint16 | 1 |  | Gateway IP address | Gateway IP address low bytes Note: useful values: 192.168 would be 49320 |  |  | Calculate this as A*2^8+B for gateway IP addr starting with bytes A.B
hreg 657 | HREG_GWIPADDR_LOW | uint16 | 1 |  | Gateway IP address | Gateway IP address low bytes/ |  |  | : Calculate this as C*2^8+D for gateway IP addr ending with bytes C.D
hreg 658 | HREG_NETMASK_HIGH | uint16 | 1 |  | Netmask | Netmask high bytes Note: useful value 65535, for bytes 255.255 |  |  | : Calculate this as A*2^8+B for netmask starting with bytes A.B
hreg 659 | HREG_NETMASK_LOW | uint16 | 1 |  | Netmask | Netmask low bytes Note: useful value 65280, for bytes 255.0 |  |  | : Calculate this as C*2^8+D for netmask ending with bytes C.D
hreg 660 | HREG_DNSIP_ADDR_HIGH | uint16 | 1 |  | DNS server address | DNS server IP high bytes |  |  | : Calculate this as A*2^8+B for ip starting with bytes A.B
hreg 661 | HREG_DNSIP_ADDR_LOW | uint16 | 1 |  | DNS server address | DNS server IP low bytes |  |  | : Calculate this as C*2^8+D for ip ending with bytes C.D
hreg 662 | Reserved
hreg 663 | Reserved
hreg 664 | Reserved
hreg 665 | Reserved
hreg 666 | Reserved
hreg 667 | HREG_DHCP_CONTROL | enumeration | 1 |  | DHCP | Dynamic Host Configuration Protocol |  |  | Value of 0 indicates DHCP is active, value of 1 indicates DHCP inactive.
hreg 668 | Reserved
hreg 669 | Reserved
hreg 670 | Reserved
hreg 671 | Reserved
hreg 672 | Reserved
hreg 673 | Reserved
hreg 674 | Reserved
hreg 675 | Reserved
hreg 676 | Reserved
hreg 677 | Reserved
hreg 678 | Reserved
hreg 679 | Reserved
hreg 680 | Reserved
hreg 681 | Reserved
hreg 682 | Reserved
hreg 683 | Reserved
hreg 684 | Reserved
hreg 685 | Reserved
hreg 686 | Reserved
hreg 687 | Reserved
hreg 688 | Reserved
hreg 689 | Reserved
hreg 690 | Reserved
hreg 691 | Reserved
hreg 692 | Reserved
hreg 693 | Reserved
hreg 694 | Reserved
hreg 695 | Reserved
hreg 696 | Reserved
hreg 697 | Reserved
hreg 698 | Reserved
hreg 699 | Reserved
hreg 700 | Reserved
hreg 701 | Reserved
hreg 702 | Reserved
hreg 703 | Reserved
hreg 704 | Reserved
hreg 705 | Reserved
hreg 706 | Reserved
hreg 707 | Reserved
hreg 708 | Reserved
hreg 709 | Reserved
hreg 710 | Reserved
hreg 711 | Reserved
hreg 712 | Reserved
hreg 713 | Reserved
hreg 714 | Reserved
hreg 715 | Reserved
hreg 716 | Reserved
hreg 717 | Reserved
hreg 718 | Reserved
hreg 719 | Reserved
hreg 720 | Reserved
hreg 721 | Reserved
hreg 722 | Reserved
hreg 723 | Reserved
hreg 724 | Reserved
hreg 725 | Reserved
hreg 726 | Reserved
hreg 727 | Reserved
hreg 728 | Reserved
hreg 729 | Reserved
hreg 730 | Reserved
hreg 731 | Reserved
hreg 732 | Reserved
hreg 733 | HREG_MODBUS_SPEED | enumeration | 1 |  | Modbus speed | Modbus RTU serial line speed | Modbus speed | Modbus RTU serial line speed | SPEED_9600 = 6, SPEED_19200 = 7, SPEED_115200 = 10
hreg 734 | HREG_MODBUS_PARITY | enumeration | 1 |  | Modbus parity | Modbus RTU serial line parity | Modbus parity | Modbus RTU serial line parity | PARITY_NONE = 1, PARITY_EVEN = 2
hreg 735 | Reserved
hreg 736 | Reserved
hreg 737 | Reserved
hreg 738 | Reserved
hreg 739 | Reserved
hreg 740 | Reserved
hreg 741 | Reserved
hreg 742 | Reserved
hreg 743 | Reserved
hreg 744 | Reserved
hreg 745 | Reserved
hreg 746 | Reserved
hreg 747 | Reserved
hreg 748 | Reserved
hreg 749 | Reserved
hreg 750 | Reserved
hreg 751 | Reserved
hreg 752 | Reserved
hreg 753 | Reserved
hreg 754 | Reserved
hreg 755 | Reserved
hreg 756 | Reserved
hreg 757 | Reserved
hreg 758 | Reserved
hreg 759 | Reserved
hreg 760 | Reserved
hreg 761 | Reserved
hreg 762 | Reserved
hreg 763 | Reserved
hreg 764 | Reserved
hreg 765 | Reserved
hreg 766 | Reserved
hreg 767 | Reserved
hreg 768 | Reserved
hreg 769 | Reserved
hreg 770 | Reserved
hreg 771 | Reserved
hreg 772 | Reserved
hreg 773 | Reserved
hreg 774 | HREG_EFFECTIVE_CIRCULATION | uint16 | 1 |  | Fan speed, circulation air | Circulation air fan's current speed |  |  | Kotilämpö, EMB, Mixbox
hreg 775 | Reserved
hreg 776 | Reserved
hreg 777 | Reserved
hreg 778 | Reserved
hreg 779 | Reserved
hreg 780 | HREG_AO1_VOLT | uint16 | 10 |  | AO1 voltage | The voltage on Analog Output 1 |  |  | NB: Only on sw 1.18 and above
hreg 781 | HREG_AO2_VOLT | uint16 | 10 |  | AO2 voltage | The voltage on Analog Output 2 |  |  | NB: Only on sw 1.18 and above
hreg 782 | HREG_AO3_VOLT | uint16 | 10 |  | AO3 voltage | The voltage on Analog Output 3 |  |  | NB: Only on sw 1.18 and above
hreg 783 | HREG_AO4_VOLT | uint16 | 10 |  | AO4 voltage | The voltage on Analog Output 4 |  |  | NB: Only on sw 1.18 and above
hreg 784 | HREG_AO5_VOLT | uint16 | 10 |  | AO5 voltage | The voltage on Analog Output 5 |  |  | NB: Only on sw 1.18 and above
hreg 785 | HREG_AO6_VOLT | uint16 | 10 |  | AO6 voltage | The voltage on Analog Output 6 |  |  | NB: Only on sw 1.18 and above
hreg 786 | HREG_AO7_VOLT | uint16 | 10 |  | AO7 voltage | The voltage on Analog Output 7 |  |  | NB: Only on sw 1.18 and above
hreg 787 | HREG_AO8_VOLT | uint16 | 10 |  | AO8 voltage | The voltage on Analog Output 8 |  |  | NB: Only on sw 1.18 and above
hreg 788 | HREG_DI9_PULSE_CNT | uint16 | 1 |  | DI9 pulse count | Number of pulses detected on DI9 |  |  | NB: Only on sw 1.18 and above
hreg 789 | HREG_DI_BITMAP | uint16 | 1 |  | DI1-12 and X9-GPIO1-3 status | Status bitmap of digital inputs DI1 to DI12 and GPIO pins 1-3 on connector X9 |  |  | NB: Only on sw 1.18 and above
hreg 790 | HREG_AI9_VOLT | uint16 | 10 |  | AI9 voltage | The measured voltage on Analog Input 9 |  |  | Input also known as X10_1. NB: long time constant! NB: Only on sw 1.18 and above
hreg 791 | HREG_AI10_VOLT | uint16 | 10 |  | AI10 voltage | The measured voltage on Analog Input 10 |  |  | Input also known as X10_1. NB: long time constant! NB: Only on sw 1.18 and above
hreg 792 | HREG_AI11_VOLT | uint16 | 10 |  | AI11 voltage | The measured voltage on Analog Input 11 |  |  | Input also known as X10_1. NB: long time constant! NB: Only on sw 1.18 and above
hreg 793 | HREG_AI12_VOLT | uint16 | 10 |  | AI12 voltage | The measured voltage on Analog Input 12 |  |  | Input also known as X10_1. NB: long time constant! NB: Only on sw 1.18 and above
hreg 794 | HREG_AI13_VOLT | uint16 | 10 |  | AI13 voltage | The measured voltage on Analog Input 13 |  |  | Input also known as X10_1. NB: long time constant! NB: Only on sw 1.18 and above
hreg 795 | HREG_AI14_VOLT | uint16 | 10 |  | AI14 voltage | The measured voltage on Analog Input 14 |  |  | Input also known as X10_1. NB: long time constant! NB: Only on sw 1.18 and above
hreg 796 | HREG_AI15_VOLT | uint16 | 10 |  | AI15 voltage | The measured voltage on Analog Input 15 |  |  | Input also known as X10_1. NB: long time constant! NB: Only on sw 1.18 and above
hreg 797 | HREG_AI16_VOLT | uint16 | 10 |  | AI16 voltage | The measured voltage on Analog Input 16 |  |  | Input also known as X10_1. NB: long time constant! NB: Only on sw 1.18 and above
hreg 798 | HREG_DO_BITMAP | uint16 | 1 |  | DO1-8 status | Status bitmap of digital outputs (relays) |  |  | NB: Only on sw 1.18 and above
hreg 799 | Reserved | uint16 | 1 |  | Ping register | Connection test register |  |  | This register is used by eAir web UI to test if the connection is live
COIL REGISTERS
Address | Symbol | Type | Multiplier | Bounds (raw value) | Name | Description | Title (en translation) | Help text (en translation) | Note
coil 0 | COIL_STOP |  | 1 |  | Stop | Stop the machine | Stop | Stop the machine
coil 1 | COIL_AWAY |  | 1 |  | Away mode | Set the machine to away mode | Away mode | mode
coil 2 | COIL_AWAYL |  | 1 |  | Away long mode | Set the machine to away long mode | mode | mode
coil 3 | Reserved
coil 4 | Reserved
coil 5 | Reserved
coil 6 | COIL_MAX_H |  | 1 |  | Max heating | Force the machine to heat at maximum effect. |  | Force the machine to heat at maximum effect.
coil 7 | COIL_MAX_C |  | 1 |  | Max cooling | Force the machine to cool at maximum effect. |  | Force the machine to cool at maximum effect.
coil 8 | COIL_CO2_BOOST_EN |  | 1 |  | CO2 boosting | CO2 boosting enabled | CO₂ boosting | Enable or disable CO₂ boosting
coil 9 | COIL_RH_BOOST_EN |  | 1 |  | RH boosting | Relative humidity boosting enabled | %RH boosting | Enable or disable humidity boosting
coil 10 | COIL_M_BOOST |  | 1 |  | Manual boost | Boost the fanspeeds to 100% for a period of time | Manual boost | Boost the fanspeeds to 100\% for a period of time
coil 11 | COIL_TEMP_BOOST_EN |  | 1 |  | Temperature boost | Temperature boosting enabled | Temperature boost | Enable or disable temperature boosting
coil 12 | COIL_SNC |  | 1 |  | Summer night cooling | Summer night cooling (SNC) function enabled. | Summer night cooling | Enable or disable summer night cooling
coil 13 | Reserved
coil 14 | Reserved
coil 15 | Reserved
coil 16 | Reserved
coil 17 | Reserved
coil 18 | COIL_AWAY_H |  | 1 |  | Heating | Heating enabled/disabled in AWAY mode | Heating | Supply air heating enabled or disabled in Away mode
coil 19 | COIL_AWAY_C |  | 1 |  | Cooling | Cooling enabled/disabled in AWAY mode | Cooling | Supply air cooling enabled or disabled in Away mode
coil 20 | Reserved
coil 21 | Reserved
coil 22 | Reserved
coil 23 | Reserved
coil 24 | Reserved
coil 25 | Reserved
coil 26 | Reserved
coil 27 | Reserved
coil 28 | Reserved
coil 29 | Reserved
coil 30 | COIL_LTO_ON |  | 1 |  |  | Heat recycler state (running=1, stopped = 0) |  | Heat recycler state (running=1, stopped = 0)
coil 31 | Reserved
coil 32 | COIL_HEAT_ON |  | 1 |  |  | After heater element state (On = 1, Off = 0) |  | Element status of after-heater (On = 1, Off = 0)
coil 33 | Reserved
coil 34 | Reserved
coil 35 | Reserved
coil 36 | COIL_TEMP_DECREASE |  | 1 |  | Decrease temperature | Temperature decrease function desc | Decrease temperature | Temperature decrease function desc
coil 37 | COIL_OVERTIME |  | 1 |  | Overtime | Programmatic equivalent of OVERTIME digital input. | Overtime | digital input.
coil 38 | Reserved |  | 1 |  | Emergency stop switch type | Emergency stop switch type desc | Emergency stop switch type | Emergency stop switch type desc.
coil 39 | Reserved
coil 40 | COIL_ECO_MODE |  | 1 |  | Eco mode | Eco mode desc | Eco mode | Eco mode desc.
coil 41 | COIL_ALARM_A |  | 1 |  | Alarm A | Alarm of class A active desc | Alarm A | Alarm of class A active desc. | This will be 1, if a class A alarm is active
coil 42 | COIL_ALARM_B |  | 1 |  | Alarm B | Alarm of class B active desc | Alarm B | Alarm of class B active desc. | This will be 1, if a class B alarm is active
coil 43 | COIL_CLK_PROG |  | 1 |  | Clock program | A Clock program is currently active | Clock program | A clock program is currently active
coil 44 | Reserved
coil 45 | Reserved
coil 46 | Reserved
coil 47 | COIL_SILENT_MODE |  | 1 |  | Silent mode | Silent mode desc | Silent mode settings | Enable or disable Silent mode
coil 48 | COIL_STOP_SLP_COOLING |  | 1 |  | Heater cool-off in STOP mode | Electrical heater cool-off function enabled when the machine has stopped. | mode | function enabled when the machine has stopped
coil 49 | COIL_SERVICE_EN |  | 1 |  | Service reminder | Service reminder enabled desc | Service reminder | Service reminder enabled
coil 50 | Reserved
coil 51 | Reserved
coil 52 | COIL_COOLING_EN |  | 1 |  | Cooling | Cooling function enabled | Cooling | Enable or disable active cooling of supply air (free cooling with heat recovery wheel always allowed when outside air temperature exceeds outside air temperature limit for cooling)
coil 53 | COIL_LTO_EN |  | 1 |  |  | Not used on MD. |  | Not used on MD
coil 54 | COIL_HEATING_EN |  | 1 |  | Heating | Heating function enabled | Heating | Enable or diable active heating of supply air (heating with heat recovery wheel is allowed)
coil 55 | COIL_LTO_DEFROST_EN |  | 1 |  | HRC defrosting | HRC defrosting function enabled during winter season | Defrosting | Enable or disable defrosting. Funktion is active during winterseason if enabled. Possible heatpump has got its own automatic defrost funktion.
coil 56 | Reserved
coil 57 | Reserved
coil 58 | Reserved
coil 59 | Reserved
coil 60 | Reserved
coil 61 | Reserved
coil 62 | Reserved
coil 63 | Reserved
coil 64 | Reserved
coil 65 | Reserved
coil 66 | Reserved
coil 67 | Reserved
coil 68 | Reserved
coil 69 | Reserved
coil 70 | Reserved
coil 71 | Reserved
Note on C12: uint16 indicates an unsigned value. int16 indicates that the value has a sign: values between 32768 and 65535 indicate a negative value, and you must then substract 65536 from the value to obtain the negative value. bitfield indicates that each of the 16 bits in the register must be interpretted separately, as indicated in the “notes” column. enumeration indicates a register with reserved values, as indicated in “notes” column.
Note on D12: Multiplier field indicates the scaling constant for the register. For instance, is a temperature measurement has multiplier 10, you should divide the result by 10 to obtain result in degrees Celsius.